
IEEE C37.118
Interface to the PI System

Version 1.0.2.0
Revision A 
How to Contact Us

	OSIsoft, Inc. 

777 Davis St., Suite 250

San Leandro, CA 94577 USA

Telephone

(01) 510-297-5800 (main phone)

(01) 510-357-8136 (fax) 

(01) 510-297-5828 (support phone)

techsupport@osisoft.com
Houston, TX 

Johnson City, TN 

Mayfield Heights, OH

Phoenix, AZ 

Savannah, GA

Seattle, WA

Yardley, PA
	Worldwide Offices

OSIsoft Australia

Perth, Australia

Auckland, New Zealand

OSI Software GmbH 

Altenstadt, Germany

OSI Software Asia Pte Ltd.

Singapore 

OSIsoft Canada ULC

Montreal, Canada 

OSIsoft, Inc. Representative Office

Shanghai, People’s Republic of China 

OSIsoft Japan KK

Tokyo, Japan 

OSIsoft Mexico S. De R.L. De C.V.

Mexico City, Mexico 

	Sales Outlets and Distributors

	· Brazil

· Middle East/North Africa

· Republic of South Africa

· Russia/Central Asia
	· South America/Caribbean

· Southeast Asia

· South Korea 

· Taiwan 

	

	WWW.OSISOFT.COM

	OSIsoft, Inc. is the owner of the following trademarks and registered trademarks: PI System, PI ProcessBook, Sequencia, Sigmafine, gRecipe, sRecipe, and RLINK. All terms mentioned in this book that are known to be trademarks or service marks have been appropriately capitalized. Any trademark that appears in this book that is not owned by OSIsoft, Inc. is the property of its owner and use herein in no way indicates an endorsement, recommendation, or warranty of such party’s products or any affiliation with such party of any kind.

RESTRICTED RIGHTS LEGEND
Use, duplication, or disclosure by the Government is subject to restrictions as set forth in subparagraph (c)(1)(ii) of the Rights in Technical Data and Computer Software clause at DFARS 252.227-7013

Unpublished – rights reserved under the copyright laws of the United States.

© 2007-2008 OSIsoft, Inc.
PI_C37118.doc


Table of Contents

1Introduction


3Reference Manuals


3Supported Features


6Diagram of Hardware Connection


7Principles of Operation


7Startup Process


8Loading PI Points


8Data Processing


9Data Flow to the PI System


10Multi-Threading


10Communications Plug-In’s


11Data Quality Indications


11Interface Robustness


13Installation Checklist


15Interface Installation on Windows


15Naming Conventions and Requirements


16Interface Directories


16PIHOME Directory Tree


16Interface Installation Directory


16Interface Installation Procedure


16Installing Interface as a Windows Service


17Installing Interface Service with PI ICU


19Installing Interface Service Manually


21Digital States


23PointSource


25PI Point Configuration


25Point Attributes


25Tag


25PointSource


25PointType


26Location1


26Location2


26Location3


26Location4


26Location5


26InstrumentTag


30ExDesc


30Scan


31Shutdown


31Output Points


33Performance Point Configuration


35I/O Rate Tag Configuration


35Monitoring I/O Rates on the Interface Node


35Configuring I/O Rate Tags with PI ICU (Windows)


37Configuring I/O Rate Tags Manually


37Configuring PI Point on the PI Server


37Configuration on the Interface Node


39Startup Command File


39Configuring the Interface with PI ICU


42C37118 Interface Tab


44XML Parameters


51PIC37118 XML Nodes, Elements, and Attributes


51Root Node


53LocalEndPoint Nodes


56RemoteEndPoint Nodes


57PMU Child Nodes


58Sample PIC37118.xml File


59Command-line Parameters


61Sample PIC37118.bat File


63Interface Node Clock


63Windows


65Security


65Windows


67Starting / Stopping the Interface on Windows


67Starting Interface as a Service


67Stopping Interface Running as a Service


69Buffering


69Which Buffering Application to Use


69How Buffering Works


70Buffering and PI Server Security


71Enabling Buffering on an Interface Node with the ICU


71Choose Buffer Type


72Buffering Settings


74Buffered Servers


77Installing Buffering as a Service


81Appendix A: Error and Informational Messages


81Message Logs


81Messages


81Interface Configuration Error Messages


83Point Loading Error Messages


84Communications Related Error Messages


86System Errors and PI Errors


87Appendix B: Communication Plug-In Selection


89Revision History





Introduction

This document describes the use of the IEEE C37.118 Interface to the PI system, from here on referred to as the PI C37.118 Interface. The PI C37.118 interface supports the IEEE
 C37.118/D7.3.5 Standard for Synchrophasors for Power Systems. 

The PI C37.118 interface was designed to operate with any C37.118 compliant device via an Ethernet or serial interface. Once connected to the C37.118 or Phasor Measurement Unit 
(PMU) or Phasor Data Concentrator 
(PDC) the Interface is designed to provide highly accurate measurement of electrical power quality.  Each instance of the interface can connect to multiple PDCs and / or PMUs and provide electrical measurements to the PI System.  
The IEEE C37.118 specification does not specify what electrical measurements the device must provide, it only specifies how the protocol specific data if provided must be formatted.  Therefore, each C37.118 device may provide its own unique set of phasor measurements.  The PI C37.118 Interface is capable of handling specific phasor configuration sets that are provided by the C37.118 compliant device.  

In general, the following electrical measurements and flags are typically provided by C37.118 compliant devices:
· C37.118 compliant Phasor 
data calculated at a rate defined by the PDC or PMU.

· System Frequency

· Frequency Deviation

· Frequency Rate of Change

· A, C, B magnitude and phase angle for Voltage and Current given in 16‑bit (scaled) Polar format
· A, C, B real and imaginary parts of complex number for Voltage and Current given in 16‑bit (scaled) Rectangular format

· A, C, B magnitude and phase angle for Voltage and Current given in 32‑bit IEEE floating point Polar format
· A, C, B real and imaginary parts of complex number for Voltage and Current given in 32‑bit IEEE floating point format

· Analog channel data as a 16‑bit integer (scaled) or 32‑bit IEEE floating point. The values and ranges defined by user.

· Digital channel data as a 16‑bit word with values and ranges defined by the user.
· Quality information reflecting the accuracy of the C37.118 data is available via a series of optional quality tags.

· Data Valid quality returned in the Data Valid flag (Bit 15) of the C37.118 STAT word indicates problems with the C37.118 data block. Some data in the block may be invalid or filled in.

· PMU Error quality returned in the PMU Error flag (Bit 14) of the C37.118 STAT word indicates internal errors with the PMU such as A/D calibration errors, memory errors, etc.

· PMU Sync Error quality returned in the PMU Sync flag (Bit 13) of the C37.118 word indicates a loss of external time synchronization such as the loss of satellite tracking or IRIG-B input failure.

· Data Sorting information used by PDC’s to indicate the method by which the PMU data is inserted into the data frame. This information is extracted from the Data Sorting flag (Bit 12) of the C37.118 STAT word.

· Time Quality indicator codes extracted from the Time Quality field (Bits 3-0) of the C37.118 FRACSEC word can be used with the PMU Sync Error quality and indicates the accuracy of the timestamp provided.

· Time Lock quality can be used in conjunction with the PMU Sync Error quality to determine the length of time that time sync has been lost. This information is extracted from the Unlocked Time flags (Bits 4 and 5) of the C37.118 STAT word.

· Leap Second status can be extracted from the Leap Second flags (Bits 6-4) of the C37.118 FRACSEC word indicates if a leap second is pending or occurring and indicates the direction of the leap.

· Non C37.118 measurement information can also be stored in PI.

· Interface diagnostic information

· Longitude and Latitude of the PMU.

Measured data from the PMU is time-stamped by the PMU in accordance with the C37.118 standard for C37.118 data.  Timestamp accuracy is achieved through an internal Global Positioning System (GPS) satellite receiver that synchronizes the PMU to within 1 μs of Coordinated Universal Time (UTC). 
If a PDC or PMU indicates a data quality or time synchronization issue by setting any of the Data Valid, PMU Error, PMU Sync Error or Data Sorting Type flags in the STAT word, the interface can do one of the following. This behavior is controlled via the XML configuration file.

· Store normally.

· Mark all PMU measurements as Questionable.

· Apply a System Digital State corresponding to the flag(s) that are set. If multiple flags are set, the most critical applies.

· Discard the measurement values.  

Multiple instances of the interface can be run on a single PI Interface Node.  However, when running multiple instances of the interface on a single node, CPU and memory allocation should be monitored to ensure the system remains in a stable state of operation.  The exact number of instances that may be run on a single PI Interface Node will vary according to hardware and network specifications. 

Note: It should be noted that the C37.118 specification is very vague with respect to the communications configuration and the various PDC / PMU vendors have implemented devices in a variety of ways.  As such, the design of the C37_117 interface uses an XML configuration file in order to provide the requisite information needed in order to establish communications with the various C37.118 devices. Check with OSIsoft to verify that your make and model of PDC or PMU has been validated for use with the C37118 interface.
Reference Manuals
OSIsoft
· PI Server manuals
· PI API Installation manual`
· UniInt Interface User Manual
Vendor

IEEE C37.118/D7.3.5 Standard for Synchrophasors for Power Systems

Supported Features

	Feature
	Support

	Part Number
	PI-IN-OS-C37.118-NTI

	* Platforms
	Windows (2000, XP, 2003) 

	APS Connector
	No

	Point Builder Utility
	No

	ICU Control
	Yes

	PI Point Types
	Digital, Int16, Int32, Float16, and Float32

	Sub-second Timestamps
	Yes

	Sub-second Scan Classes
	No (Unsolicited Only)

	Automatically Incorporates PI Point Attribute Changes
	Yes

	Exception Reporting
	No

	Outputs from PI
	No

	Inputs to PI: Scan-based / Unsolicited / Event Tags
	Unsolicited

	Supports Questionable Bit
	Yes

	Supports Multi-character PointSource
	Yes

	Maximum Point Count
	No

	* Uses PI SDK
	No

	PINet String Support
	No

	* Source of Timestamps
	C37.118 Datastream

	* History Recovery
	No

	* UniInt-based

Disconnected Startup

SetDeviceStatus
	Yes 

Yes

Yes

	Failover
	No

	* Vendor Software Required on PI Interface Node / PINet Node
	No

	* Vendor Software Required on Foreign Device
	No

	* Vendor Hardware Required
	Yes

	* Additional PI Software Included with Interface
	No

	* Device Point Types
	Digital, Float, Integer (including Real and Imaginary)

	Serial Based Interface
	Yes


* See paragraphs below for further explanation.

Platforms
The Interface is designed to run on the above mentioned Microsoft Windows operating systems.

Uses PI SDK
The PI SDK and the PI API are bundled together and must be installed on each PI Interface node.  This Interface does not specifically make PI SDK calls.

Source of Timestamps

Timestamps are acquired from the C37.118 data stream.
Supports Questionable bit

The interface can be configured to mark data as questionable when any of the status flags in the C37.118 STAT word are set.
UniInt-based

UniInt stands for Universal Interface. UniInt is not a separate product or file; it is an OSIsoft-developed template used by developers, and is integrated into many interfaces, including this interface. The purpose of UniInt is to keep a consistent feature set and behavior across as many of OSIsoft’s interfaces as possible. It also allows for the very rapid development of new interfaces. In any UniInt-based interface, the interface uses some of the UniInt‑supplied configuration parameters and some interface-specific parameters. UniInt is constantly being upgraded with new options and features.

The UniInt Interface User Manual is a supplement to this manual.

SetDeviceStatus

The PI C37.118 Interface is built with UNIINT 4.3.0.36 or higher.  New functionality has been added to support health tags. The Health tag, which is a string tag with the point attribute Exdesc = [UI_DEVSTAT], is used to represent the status of the source device. The following events can be written into this tag:    


a)  “Good” - the interface is properly communicating and reading data from all configured PMUs.  

b)  “1 | Starting | UI #.#.#.#” – The interface is currently starting up. 

c)  “3 | 1 devices(s) in error | REP: 1 LEP 1” – The connection to one or more PMUs has failed.

d)  “4 | Intf Shutdown” – The interface has been shutdown.

Please refer to the UniInt Interface User Manual.doc file for more information on how to configure health points.

Vendor Hardware Required

C37.118 compliant Phasor Measurement Unit or Phasor Data Concentrator are required for proper communication with this interface.
Device Point Types

The interface supports all Phasor, Analog and Digital channels plus frequency and frequency rate of change. Frequency error is also computed by the interface.
Serial-Based Interfaces

This interface can run either with a serial connection or Ethernet network connection.

Server class machines often have inferior serial ports.  Server class machines are not required for most interfaces and should not be used, especially not when serial port connections are required.
Diagram of Hardware Connection

[image: image1.emf]PI C37.118 Interface

text

PDC/PMU

PI Data Archive

PDC/PMU

C37.118 Data C37.118 Data C37.118 Data

PDC/PMU

PDC/PMU

PDC/PMU

PDC/PMU

PI Interface 

Node

PI Server 

Node

PI API / SDK

PI Buffering

PI C37.118

Communications 

Plugin(dll)

PI C37.118

Communications 

Plugin(dll)

PI C37.118

Communications 

Plugin(dll)

PDC / PMU Model specific Plug-In’s 

handle differences in application 

layer implementation between 

different vendors.

Communications 

Plug-In’s


Principles of Operation

The PI C37.118 interface is designed to request and process data from C37.118 compliant devices.  The PI C37.118 interface is a real-time based interface.  The interface operations can be categorized into the following list of sub-operations:

· Startup Process

· Loading PI Points
· Data Processing

· Data Flow to the PI System
· Data Quality Indicators
· Interface Robustness

A more detailed explanation of the list of sub-operations for this interface is provided in this section.

Startup Process

The PI C37.118 Interface must be configured in accordance with the Startup Command File (.bat file) and the Interface Configuration File (XML configuration file).  Each instance of the C37118 interface is assigned a specific identification number and/or point source, which are correlated with the interface-specific startup file parameters /id, /ps and /configfile.
The C37118 Interface establishes the initial connection to PI and reconnects to PI in the event that the connection is lost for some reason. If the Interface is started while the PI Server is down, the Interface will periodically try to establish a connection until the PI Server is up.

The interface is designed to make use of a configuration file to set up the internal operation of the interface.  The configuration file is written in XML format. A PI Interface Configuration Utility (ICU) plug-in is available for this interface to assist in the configuration of both the startup batch file and the interface (XML) configuration file. The use of this ICU Control (highly recommended) is described in the Startup Command File section of this document. 
When the interface starts, it parses the passed command line parameters searching for the requested XML configuration file specified via the /configfile command line parameter. If the /configfile=<UNCpath> is not found a default file name, pic37118.xml, is assumed. The configuration file is then parsed and the interface instantiates the internal structures required for communication with the C37.118 PDC and / or PMUs.

A description of the internal structures and terms utilized by the interface are described below.
LocalEndPoint

The LocalEndPoint represents the local (interface side) of a physical network or serial connection to a C37.118 device. Each LocalEndPoint should contain the various LocalEndPoint attributes as well as a single RemoteEndPoint leaf node which contains the RemoteEndPoint attributes..

RemoteEndPoint

The RemoteEndPoint object represents the remote (C37.118 device) side of a physical connection. Currently there can only be one RemoteEndPoint configured for each LocalEndPoint.

PMU

The PMU object represents a C37.118 Phasor Data Concentrator (PDC) or Phasor Measurement Unit (PMU). If the RemoteEndPoint is a PDC, there can be multiple PMU objects associated with the RemoteEndPoint.
Loading PI Points
When the PI C37.118 Interface starts, it searches the PI Point Database for points that belong to the Interface and a point list is created for the interface. The primary method of establishing a mapping between a PI Point and a C37.118 device is through configuration of the Location2, Location3, Location5, InstrumentTag and UserInt1 PI Point attributes. The correlation between the above attributes and the various C37.118 measurements are listed in the PI Point Configuration section of this document. 
PI Points for this interface have a one-to-one correspondence with electrical measurements available from the C37.118 device.  There can only be one PI Point for receiving a specific measurement from a given C37.118 device. 

For example: If a PI Point is configured to read the magnitude from a Phasor channel named “Phasor Volt CH-A”  (InstrumentTag=PhasorMag\Phasor Volt CH-A) from a specific LocalEndPoint, RemoteEndPoint and PMU combination (Location2, Location3 and Location5) there can be no other PI Points specified with identical attributes. 
Once the interface loads a PI Point, any additional PI Points having the same attributes as a previously loaded PI Point will be rejected by the interface and the interface will log an error message. Refer to Appendix A: Error and Informational Messages for more details on messages associated with Loading PI Points.
Data Processing

The PI C37.118 Interface processes C37.118 formatted data messages as defined in the IEEE C37.118 specification. The input data is parsed to provide the:

· Real and Imaginary part of the complex number for each Phasor channel if the PDC / PMU is configured to send phasor measurements in rectangular format.
· Magnitude and Phase Angle for each Phasor channel for each Phasor channel if the PDC / PMU is configured to send phasor measurements in polar format.
· Analog channel data

· Digital channel data

· System Frequency

· Frequency deviation (calculated by interface)
· Frequency Rate of Change

Note: If the PMU is configured to send data in rectangular format, the interface will compute s the polar coordinates and vice versa if the PMU is configured to send data in polar format.

In addition to the data parsed from the C37.118 data, the interface also provides for input of C37.118 configuration data from the CONFIG2 data block. The configuration data is parsed to provide:

· Configuration change count from CFGCNT
· Data transmit rate from DATA_RATE
· Nominal frequency (50Hz / 60Hz )
Optional data quality tags can be configured to receive information related to the quality of the C37.118 data. This quality information is extracted from the time quality, leap second status and STAT fields of the C37.118 data stream. These include the following:
· Data Valid
· PMU Error

· PMU Sync

· Data Sorting

· Time Unlocked Time
· Trigger Reason

The interface can also store geographical information regarding the location of the PMU if defined in the Interface Configuration File. The Latitude and Longitude of the PMU can be defined in decimal form in the configuration file and stored in PI.  
Data Flow to the PI System

Data flow from the C37.118 device to the PI System is unsolicited.  The following is an explanation of the sequence of events that takes place in order to get the data from the C37.118 device interface into the PI System.  
Phasor data from C37.118 is sent to the interface at a rate which is configured in the C37.118 device and is typically 20, 30, 60 or 120 times per second for 60Hz systems and 25, 50, and 100 times per seconds for 50Hz systems. 
Once the interface communications plug-in issues the start data command, which is issued at startup and after any communications failure, the C37.118 device starts sending data at the configured rate.
The communications plug-in then processes the incoming data stream. Each C37.118 data frame is processed and the size and CRC verified. The C37.118 frame is then queued to the main interface thread.
The main interface thread of the interface parses and processes C37.118 data frames in the incoming data queue and sends the results to the PI System on a real-time basis.  This means that device data, after processing, will immediately be sent and available in the PI System. 
The illustration below shows a graphical representation of data flow from the C37.118 PDC / PMU device to the PI System. 


[image: image2.emf]PDC or 

PMU

PI_C37118

Interface

PI Archive

Raw-Data and Timestamp

Process Raw-Data

Update PI System


Multi-Threading

The PI C37.118 Interface is designed as a multithreaded implementation. Communications with the PDC / PMU is handled in separate threads from the main interface body. Depending on the Communications Plug-In being used, there will be either 1 or 2 communications threads created. If commands and command responses operate on the same communications port as the C37.118 data stream, a single communications thread will handle all communications with the PDC / PMU. If commands and command responses operate on independent ports then 2 communications threads are created. One thread handles commands and command responses and the second is dedicated to receiving the C37.118 data stream. Data from each communications thread is buffered and then serialized through the main interface thread. This must be done because the PI API is not currently thread safe.

Communications Plug-In’s
The PI C37.118 Interface utilizes “Communications Plug-In’s” to handle differences in the application layer communications for various PDCs and PMUs. This is necessary because the IEEE C37.118 specification does not dictate the implementation.
The following describes the plug-ins distributed with the PI C37.118 Interface.
PIC37118_Comm001

This plug-in is used for devices that use a single socket via either UDP or TCP for commands, command responses and measurement data. This plug-in is also used for serial connections.
PIC37118_Comm002

This plug-in is used for devices that use two sockets. Commands, command responses are performed via one socket and measurement data is returned via a separate socket. Typically the device uses TCP for the commands and UDP for the measurement data.
PIC37118_Comm003

This plug-in is used for devices that use a single socket via either UDP or TCP but do not support output commands. Once the device starts it sends data automatically to a predetermined address and port. This is referred to as “Autonomous Mode” on most devices. It expects that the CONFIG2 block is sent periodically along with the measurement data.
Data Quality Indications

The PI C37.118 Interface provides multiple methods to monitor the quality of the data being provided by the C37.118 PDC / PMU. 

The following types of data quality indications are available. All of these are optional and can be used alone or in conjunction with other data quality indicators.

· Quality Tags – Quality tags are PI tags that are separate from data tags.

· Conditional Data Tag Status – The interface can be configured to apply one of 4 different rules in response to one or more of the data quality flags being set.
Interface Robustness

The C37118 interface is designed to be robust in regards to data acquisition.  If the interface determines that Phasor data has not been received within the time specified by the DataTimeout parameter in the configuration file, an entry will be made to the pipc.log file and the interface will attempt to restart the C37.118 phasor data stream. Upon receipt of a successful response from the C37.118 device, the interface will begin processing data and log a message to the pipc.log file.  The interface will retry failed connection attempts until data flow is restored but will not log further connection failure messages until data flow is restored.  Refer to Appendix A: Error and Informational Messages for more details on messages associated with transmission loss.

The interface is configured to make use of the WriteIOTimeout parameter in the interface configuration file.  This parameter informs the interface whether to write an error state to PI Points when data from the device is not received after the period specified by the DataTimeout parameters.  Setting WriteIOTimeout=1, the default, will cause the system digital state of “I/O Timeout” to be written to PI Points.  Alternately, setting WriteIOTimeout=0 will inform the interface not to update PI Points during transmission loss C37.118 data. The default behavior is to write “I/O Timeout” for all measured values.
Installation Checklist

For those users who are familiar with running PI data collection interface programs, this checklist helps get the Interface running. If not familiar with PI interfaces, return to this section after reading the rest of the manual in detail.

1. Install the PI Interface Configuration Utility (which installs PI SDK and PI API)

2. Verify that PI API has been installed.

3. Install the interface.

4. Define digital states.  
Example configuration files are provided with the interface installation kit.

5. Modify example interface XML configuration file as needed. 

6. Choose a point source.  

7. Configure PI points. 
Location1 is the interface instance.
Location2 is the LocalEndPoint ID.
Location3 is the RemoteEndPoint ID. This attribute always reflects the IDCODE of PDC / PMU contained in word 3 of the C37.118 data stream. If the connected device is a PMU (versus a PDC), Location3 and Location5 will be the same.  
Location4 is not used.
Location5 is the PMU ID. This attribute will always match the IDCODE of the PMU that is the source of the data.
InstrumentTag specifies the specific measurement and type.
ExDesc is not used.
UserInt1 is not used.
UserInt2 is not used.
8. Configure the interface using the PI ICU utility or edit startup command file manually. It is recommended to use PI ICU whenever possible.
9. Configure I/O Rate tag.
10. Set interface node clock.

11. Set up security.

12. Start the interface without buffering.

13. Verify data.

14. Stop interface, start buffering, start interface.

Interface Installation on Windows 
OSIsoft recommends that interfaces be installed on PI Interface Nodes instead of directly on the PI Server node. A PI Interface Node is any node other than the PI Server node where the PI Application Programming Interface (PI API) has been installed (see the PI API manual). With this approach, the PI Server need not compete with interfaces for the machine’s resources. The primary function of the PI Server is to archive data and to service clients that request data. 

After the interface has been installed and tested, Bufserv should be enabled on the PI Interface Node (once again, see the PI API manual). Bufserv is distributed with the 
PI API. It is a utility program that provides the capability to store and forward events to a PI Server, allowing continuous data collection when communication to the PI Server is lost. Communication will be lost when there are network problems or when the PI Server is shut down for maintenance, upgrades, backups, or unexpected failures. 

In most cases, interfaces on PI Interface Nodes should be installed as automatic services. Services keep running after the user logs off. Automatic services automatically restart when the computer is restarted, which is useful in the event of a power failure.

The guidelines are different if an interface is installed on the PI Server node. In this case, the typical procedure is to install the PI Server as an automatic service and install the interface as an automatic service that depends on the PI Update Manager and PI Network Manager services. This typical scenario assumes that Bufserv is not enabled on the PI Server node. Bufserv can be enabled on the PI Server node so that interfaces on the PI Server node do not need to be started and stopped in conjunction with PI, but it is not standard practice to enable buffering on the PI Server node. See the UniInt Interface User Manual for special procedural information.

Naming Conventions and Requirements

In the installation procedure below, it is assumed that the name of the interface executable is pic37118.exe and that the startup command file is called pic37118.bat. 

When Configuring the Interface Manually

When configuring the interface manually it is customary for the user to rename the executable and the startup command file when multiple copies of the interface are run. For example, pic371181.exe and pic371181.bat would typically be used for interface number 1, pic371182.exe and pic371182.bat for interface number 2, and so on. When an interface is run as a service, the executable and the command file must have the same root name because the service looks for its command-line parameters in a file that has the same root name.
Interface Directories

PIHOME Directory Tree

The PIHOME directory tree is defined by the PIHOME entry in the pipc.ini configuration file. This pipc.ini file is an ASCII text file, which is located in the %windir% directory. A typical pipc.ini file contains the following lines:
[PIPC]
PIHOME=c:\pipc
The above lines define the \pipc directory as the root of the PIHOME directory tree on the C: drive. OSIsoft recommends using \pipc as the root directory name. The PIHOME directory does not need to be on the C: drive.

Interface Installation Directory

Place all copies of the interface into a single directory. The suggested directory is:

PIHOME\Interfaces\C37118\
Replace PIHOME with the corresponding entry in the pipc.ini file.

Interface Installation Procedure

The PI C37,118 Interface setup program uses the services of the Microsoft Windows Installer. Windows Installer is a standard part of Windows 2000 and greater operating systems. To install, run the C37118_x.x.x.x.exe installation kit. 

Installing Interface as a Windows Service

The PI C37.118 Interface service can be created, preferably, with the PI Interface Configuration Utility, or can be created manually.
Installing Interface Service with PI ICU
The PI Interface Configuration Utility provides a user interface for creating, editing, and deleting the interface service:
[image: image3.png], Pl-Interface Configuration Utility - PIC371181 -[o) x|

Interface Tooks Help

DEXd)eopR|@e

Inteitace: [FI-C371181 (PIC371181) > piserver =] _Rename
Tope: [Grms =] PEEECHe Pl ServerComnecton tatus—
Descrption pisever
itesble
Versons  [FIC37118.e%e verson 1001 i veson 43015
[Gonsd | Senvics Confguaton
Ui S -Statup Type | [ Create/ Remove
Sevicenane:  [FICS7ITET of
FISDK Hl [ Ao Create
Discornected Statup | Dislaprames  [PLRICITITE1 © anul
eebm Iy e © Diabled Femoye
Peromance Poits | Password
Perfomance Courters
Corfim password
Health Points & Installed services
carrie Depancencies: [t BackupE rechPCavie =
e s 815 =i
e ot P i Saice
[ Boner
bty
s &
o 3
Pluler Server

Close. Apply

[Ready [Service Uninstalled [PIC371181 - Not Installed v





Service Configuration

Service name

The Service name box shows the name of the current interface service. This service name is obtained from the interface executable.
ID

This is the service id used to distinguish multiple instances of the same interface using the same executable. 
Display name

The Display Name text box shows the current Display Name of the interface service.  If there is currently no service for the selected interface, the default Display Name is the service name with a “PI-” prefix. Users may specify a different Display Name. OSIsoft suggests that the prefix “PI-” be appended to the beginning of the interface to indicate that the service is part of the OSIsoft suite of products.
Log on as

The Log on as text box shows the current “Log on as” Windows User Account of the interface service.  If the service is configured to use the Local System account, the Log on as text box will show “LocalSystem.” Users may specify a different Windows User account for the service to use.
Password

If a Windows User account is entered in the Log on as text box, then a password must be provided in the Password text box, unless the account requires no password.

Confirm Password

If a password is entered in the Password text box, then it must be confirmed in the Confirm Password text box.
Startup Type

The Startup Type indicates whether the interface service will start automatically or needs to be started manually on reboot.  

· If the Auto option is selected, the service will be installed to start automatically when the machine reboots.  

· If the Manual option is selected, the interface service will not start on reboot, but will require someone to manually start the service.  

· If the Disabled option is selected, the service will not start at all.  

Generally, interface services are set to start automatically.

Dependencies

The Installed services list is a list of the services currently installed on this machine. Services upon which this Interface is dependent should be moved into the Dependencies list using the [image: image4.png]


 button. For example, if PI API Buffering is running, then “bufserv” should be selected from the list at the right and added to the list on the left. To remove a service from the list of dependencies, use the [image: image5.png]


 button, and the service name will be removed from the “Dependencies” list.

When the PI Interface is started (as a service), the services listed in the dependency list will be verified as running (or an attempt will be made to start them). If the dependent service(s) cannot be started for any reason, then the PI interface service will not run. 

Note: Please see the PI Log and Operating System Event Logger for messages that may indicate the cause for any server not running as expected.   

[image: image6.png]


 - Add Button

To add a dependency from the list of Installed services, select the dependency name, and click the Add button.

[image: image7.png]


 - Remove Button

To remove a selected dependency, highlight the service name in the Dependencies list, and click the Remove button.  

The full name of the service selected in the Installed services list is displayed below the Installed services list box.

Create

The Create button adds the displayed service with the specified Dependencies and with the specified Startup Type.  

Remove 

The Remove button removes the displayed service. If the service is not currently installed, or if the service is currently running, this button will be grayed out.  

Start or Stop Service

To Start or Stop an interface service, use the Start button [image: image8.bmp] and a Stop button [image: image9.bmp] on the ICU toolbar. If this interface service is not currently installed, these buttons will remain grayed out until the service is added. If this interface service is running, the Stop button is available. If this service is not running, the Start button is available.

The status of the Interface service is indicated in the lower portion of the PI ICU dialog.
[image: image10.png]|Ready [Running [PIC371181 - Installed





[image: image45.png]


[image: image46.png]



Installing Interface Service Manually
Help for installing the interface as a service is available at any time with the command:
PIC37118.exe –help 

Change to the directory where the PIC371181.exe executable is located. Then, consult the following table to determine the appropriate service installation command.
	Windows Service Installation Commands on a PI Interface Node or a PI Server Node
with Bufserv implemented

	Manual service
	PIC37118.exe –install –depend “tcpip bufserv”

	Automatic service
	PIC37118.exe –install –auto –depend “tcpip bufserv”

	*Automatic service with service id
	PIC37118.exe –serviceid X –install –auto –depend “tcpip bufserv”

	Windows Service Installation Commands on a PI Interface Node or a PI Server Node
without Bufserv implemented

	Manual service
	PIC37118.exe –install –depend tcpip

	Automatic service
	PIC37118.exe –install –auto –depend tcpip

	*Automatic service with service id
	PIC37118.exe –serviceid X –install –auto –depend tcpip


*When specifying service id, the user must include an id number. It is suggested that this number correspond to the interface id (/id) parameter found in the interface .bat file.
Check the Microsoft Windows services control panel to verify that the service was added successfully. The services control panel can be used at any time to change the interface from an automatic service to a manual service or vice versa. 

Digital States

For more information regarding Digital States, refer to the PI Server documentation.

Digital State Sets

PI digital states are discrete values represented by strings. These strings are organized in PI as digital state sets. Each digital state set is a user-defined list of strings, enumerated from 0 to n to represent different values of discrete data. For more information about PI digital tags and editing digital state sets, see the PI Server manuals.

An interface point that contains discrete data can be stored in PI as a digital tag. A Digital tag associates discrete data with a digital state set, as specified by the user.

Interface Specific Digital Sets

If quality tags are being used, quality tag specific digital sets must be created. Example structure files are provided to assist in the configuration. Configuration files for the following digital state sets are provided.
· PIC37118_CompositeQual
· PIC37118_ConfigChange

· PIC37118_ConnectState
· PIC37118_DataSorting
· PIC37118_DataVaild
· PIC37118_LeapSecond
· PIC37118_NominalFreq
· PIC37118_PMUError
· PIC37118_SyncError
· PIC37118_Timelock
· PIC37118_TimeQuality
· PIC37118_Trigger

The example structure files provided can be used to import the sets into PI using SMT. They are located in the Configuration Files subdirectory of the specified installation location. 
System Digital State Set

Similar to digital state sets is the system digital state set. This set is used for all tags, regardless of type to indicate the state of a tag at a particular time. For example, if the interface receives bad data from an interface point, it writes the system digital state bad input to PI instead of a value. The system digital state set has many unused states that can be used by the interface and other PI clients. Digital States 193-320 are reserved for OSIsoft applications.
PointSource 
The PointSource is a unique, single or multi-character string that is used to identify the PI point as a point that belongs to a particular interface. For example, the string Boiler1 may be used to identify points that belong to the MyInt Interface. To implement this, the PointSource attribute would be set to Boiler1 for every PI Point that is configured for the MyInt Interface. Then, if /ps=Boiler1 is used on the startup command-line of the MyInt Interface, the Interface will search the PI Point Database upon startup for every PI point that is configured with a PointSource of Boiler1. Before an interface loads a point, the interface usually performs further checks by examining additional PI point attributes to determine whether a particular point is valid for the interface. For additional information, see the /ps parameter.
Case-sensitivity for PointSource Attribute
If the interface is running on a PINet node, use a capital letter (or a case-insensitive character such as a number, a question mark, etc.) for the PointSource attribute when defining points. For all other scenarios, the case of the PointSource is insignificant. 

In all cases, the PointSource character that is supplied with the /ps command-line argument is not case sensitive. That is, /ps=P and /ps=p are equivalent. It is only necessary to be careful with the case of the PointSource during point definition and only if the Interface will be running on a PINet node communicating to a PI Server.

Reserved Point Sources

Several subsystems and applications that ship with PI are associated with default PointSource characters. The Totalizer Subsystem uses the PointSource character T, the Alarm Subsystem uses G and @, Random uses R, RampSoak uses 9, and the Performance Equations Subsystem uses C. Do not use these PointSource characters or change the default point source characters for these applications. Also, if a PointSource character is not explicitly defined when creating a PI point; the point is assigned a default PointSource character of Lab (PI 3). Therefore, it would be confusing to use Lab as the PointSource character for an interface.
Note: Do not use a point source character that is already associated with another interface program. However it is acceptable to use the same point source for multiple instances of an interface.
PI Point Configuration

The PI point is the basic building block for controlling data flow to and from the PI Server. A single point is configured for each measurement value that needs to be archived. 

Point Attributes

Use the point attributes below to define the PI Point configuration for the Interface, including specifically what data to transfer.
Tag
A tag is a label or name for a point. Any tag name can be used in accordance with the normal PI point naming conventions.

Length

The length of the Tag field is limited by the version of the PI API, the version of the PI Server, and sometimes by a specific Interface.  The table below explains this in more detail.  When the maximum possible lengths differ for the software installed on site, the shortest length applies. 

	PI API
	PI Server
	Maximum Length

	1.6 or higher
	3.4.370.x or higher
	1023

	1.6 or higher
	Below 3.4.370.x
	255

	Below 1.6
	3.4.370.x or higher
	255

	Below 1.6
	Below 3.4.370.x
	255


PointSource
The PointSource is a single, unique character(s) string that is used to identify the PI point as a point that belongs to a particular interface. For additional information, see the /ps command-line argument and the “Point Source” section.

PointType
Typically, device point types do not need to correspond to PI point types. For example, integer values from a device can be sent to floating point or digital PI tags. Similarly, a floating-point value from the device can be sent to integer or digital PI tags, although the values will be truncated. 

Float16, float32, float 64, int16, int32, digital point types are supported. For more information on the individual PointTypes, see PI Server manuals.

Location1
Location1 indicates to which copy of the interface the point belongs. The value of this attribute must match the /id startup parameter.
Location2
Location2 specifies the ID of the LocalEndPoint. This corresponds to the Id parameter of the corresponding LocalEndPoint section in the interfaces XML configuration file. This attribute is used by the interface to uniquely identify the LocalEndPoint object and does not correspond to any C37.118 attributes. 
Note: The Id Must Be Unique among all LocalEndPoint sections in the configuration file.

Location3

Location3 specifies the ID of the RemoteEndPoint. This corresponds to the IdCode attribute of the corresponding RemoteEndPoint section in the interfaces XML configuration file and must match the configured IDCODE on the PDC / PMU hardware. If the C37.118 device is a PDC there will most likely be multiple PMUs. This attribute should match the IDCODE field for the PDC and not the PMU.

Location4
The C37.118 Interface is exception based only. Location 4 should be set to zero for all points.

Location5
Location5 specifies the PMU ID. This attribute must match the IDCODE field for the PMU in the C37.118 CONFIG2 message as well as the IdCode attribute in the PMU section of the XML configuration file. The value for this will be determined when configuring PDC or PMU. If the C37.118 device is a PMU, versus a PDC, this value will typically match the IDCODE for the RemoteEndPoint specified in location3.

If the device is a PDC, each PMU being collected by the PDC must have a unique IDCODE field configured.
InstrumentTag
The InstrumentTag attribute specifies the specific C37.118 measurement to be stored in PI. The attribute contains two elements. The first is the Measurement Type and the second is the specific channel name, REP or PMU measurement and is in the format of MeasurementType\Measurement.

Length

The length of the InstrumentTag field is limited by the version of the PI API, the version of the PI Server, and sometimes by a specific Interface.  The table below explains this in more detail.  When the maximum possible lengths differ for the software installed on site, the shortest length applies.

	PI API
	PI Server
	Maximum Length

	1.6 or higher
	3.4.370.x or higher
	1023

	1.6 or higher
	Below 3.4.370.x
	32

	Below 1.6
	3.4.370.x or higher
	32

	Below 1.6
	Below 3.4.370.x
	32


Measurement Types

There are five primary Measurement Types that the interface supports. They are:

· Phasor – The interface will read one of the C37.118 Phasor channels. There are four subtypes for phasor measurements.
· Analog – The interface will read one of the C37.118 Analog channels

· Digital – The interface will read one of the C37.118 Digital channels. UserInt1 and UserInt2 are used in combination with this attribute to specify a specific bit(s) to be stored in PI.

· PMU – PMU measurement types are those which are not Phasor, Analog or Digital and are related to the PMU. These include PMU values such Frequency (FREQ) and Frequency rate of Change (DFREQ), Configuration data such as the data scheduling time base (TIME_BASE) field from the C37.118 CONFIG message and interface configuration data from the XML configuration file such as the PMU Latitude and Longitude.

· REP – REP measurement types are those related to the RemoteEndPoint. These include connection status as well as time quality. 

For Phasor measurement types, the interface can return four different measurements, Real, Imaginary, Magnitude and Phase Angle.

The following table illustrates the valid MeasurementType keywords for use in the InstrumentTag attribute. The keywords are not case sensitive.
	MeasurementType

	Keyword
	Description

	PhasorReal
	Returns the Real measurement for the specified Phasor Channel.

	PhasorImag
	Returns the Imaginary measurement for the specified Phasor Channel.

	PhasorMag
	Returns the Magnitude measurement for the specified Phasor Channel.

	PhasorAngle
	Returns the Phase Angle measurement for the specified Phasor Channel

	Analog
	Returns the measurement from the specified Analog Channel.

	Digital
	Returns the Digital measurement from the specified Digital Channel. The UserInt1 and UserInt2 attributes are used to determine the exact bit(s) to extract.

	PMU
	The interface returns one of the PMU measurements. 

	REP
	Remote End Point related tag


   InstrumentTag Measurement Type Keywords

Measurements

For Phasor, Analog and Digital Measurement Types, the user must specify the C37.118 channel name from which the interface will collect data. Channel names will vary by vendor. 
For the PMU and REP Measurement types the user must enter one of the PMU or REP Measurement keyword described below.

The C37.118 specification defines the channel names to be a 16 byte ASCII string that can have embedded as well as trailing spaces. The interface strips any trailing spaces but leaves any embedded spaces. The interface also treats the strings as case insensitive. If for example a PMU has a channel name of 'Watts CH-A      ', the user would specify 'Watts CH-A' for the Measurement element of the InstrumentTag. 'watts ch-a' would also be valid in this example.

For PMU MeasurementTypes tags the interface will store various data from the C37.118 data stream, CONFIG1 and CONFIG2 blocks and configuration data from the XML configuration file. The follow table shows the valid values for the Measurement field when the MeasurmentType field is PMU.  

	PMU Measurement Values

	Keyword
	Description

	FREQ
	System frequency (FREQ) from C37.118 data stream

	DFREQ
	Frequency Rate of Change (DFREQ) from C37.118 data stream.

	FREQERR
	Frequency error calculated from FREQ – Nominal Frequency as defined by FNOM (50 or 60).

	CFGCNT
	Configuration change count (CFGCNT) from last CONFIG block

	CONFIGFLAG
	Digital tag that is set to 1 when the configuration change flag (bit 10) in the STAT word is true.

	FNOM
	Nominal line frequency (FNOM) from last CONFIG block

	DATA_RATE
	Date rate (DATA_RATE) from last CONFIG block

	LATITUDE
	PMU Latitude (-90.0-90.0) from XML configuration file

	LONGITUDE
	PMU Longitude (-180.0-180.0) from XML configuration file

	TIMELOCK
	Digital tag receives the Unlocked Time quality bits (5-4) from the STAT word. A sample digital set definition file PIC37118_Timelock.csv is provided with the interface to assist in creating the required digital state set for this tag. This file can be used to import the state set into PI using the Digital States Plug-In in SMT.

	TRIGGER
	Digital tag receives the Trigger Reason bits (3-0) from the STAT word. A sample digital set definition file PIC37118_Trigger.csv is provided with the interface to assist in creating the required digital state set for this tag. This file can be used to import the state set into PI using the Digital States Plug-In in SMT.

	DATAVALID
	Digital tag receives the Data Validity bit (15) from the STAT word. A sample digital set definition file PIC37118_DataValid.csv is provided with the interface to assist in creating the required digital state set for this tag. This file can be used to import the state set into PI using the Digital States Plug-In in SMT.

	PMUERROR
	Digital tag receives the PMU Error bit (14) from the STAT word. A sample digital set definition file PIC37118_PMUError.csv is provided with the interface to assist in creating the required digital state set for this tag. This file can be used to import the state set into PI using the Digital States Plug-In in SMT.

	SYNCERROR
	Digital tag receives the PMU Sync Error bit (13) from the STAT word. A sample digital set definition file PIC37118_SyncError.csv is provided with the interface to assist in creating the required digital state set for this tag. This file can be used to import the state set into PI using the Digital States Plug-In in SMT.

	DATASORTING
	Digital tag receives the Data Sorting bit (12) from the STAT word. A sample digital set definition file PIC37118_DataSorting.csv is provided with the interface to assist in creating the required digital state set for this tag. This file can be used to import the state set into PI using the Digital States Plug-In in SMT.

	COMPOSITEQUAL
	Digital tag receives a composite status from the Data Valid, PMU Error, Sync Error and Data Sorting flags. If any of these flags are set, the value of this tag will be set to 1. Otherwise it will be zero.

This tag is intended to be used to enable the user to make a single check for any quality related issues and then do further checking only if needed.

A sample digital set definition file PIC37118_CompositeQuality.csv is provided with the interface to assist in creating the required digital state set for this tag. This file can be used to import the state set into PI using the Digital States Plug-In in SMT.


Measurement Values for PMU Measurement Type Tags

	REP Measurement Values

	Keyword
	Description

	TIMEQUAL
	Digital tag receives the Qime Quality bits (3-0) from the time quality flags. A sample digital set definition file PIC37118_TimeQuality.csv is provided with the interface to assist in creating the required digital state set for this tag. This file can be used to import the state set into PI using the Digital States Plug-In in SMT.

	LEAPSEC
	Digital tag receives the Leap Second quality bits (6-4) from the time quality flags. A sample digital set definition file PIC37118_LeapSecond.csv is provided with the interface to assist in creating the required digital state set for this tag. This file can be used to import the state set into PI using the Digital States Plug-In in SMT.

	CONNECTSTATE
	Digital tag receives the current connection state. A sample digital set definition file PIC37118_ConnectState.csv is provided with the interface to assist in creating the required digital state set for this tag. This file can be used to import the state set into PI using the Digital States Plug-In in SMT.

	EVENTSEQ
	Integer tag intended for diagnostic purposes to verify that the interface is not losing messages. It records the sequence number of the message within a second. For example: If the update rate for the PMU is set to 30hz, the expected values would cycle from 0 to 29 without missing any values.


Measurement Values for REP Measurement Type Tags

ExDesc
This attribute is not used by the PI C37.118 interface.
Scan 

The Scan attribute has the default value of 1, indicating that the Interface should collect data for the point.  Setting the Scan attribute to 0 turns data collection off.  If the Scan attribute is 0 when the interface starts, the Interface writes SCAN OFF to the point.  If the user changes the Scan attribute from 1 to 0 while the interface is running, the Interface also writes SCAN OFF.
There is one other situation, which is independent of the Scan attribute, where UniInt will write SCAN OFF to a PI point. If a point that is currently loaded by the interface is edited so that the point is no longer valid for the interface, the point will be removed from the interface, and SCAN OFF will be written to the point. For example, if the PointSource of a PI point that is currently loaded by the interface is changed, the point will be removed from the interface and SCAN OFF will be written to the point.

Shutdown
The Shutdown attribute is 1 (true) by default. The default behavior of the PI Shutdown subsystem is to write the SHUTDOWN digital state to all PI points when PI is started. The timestamp that is used for the SHUTDOWN events is retrieved from a file that is updated by the Snapshot Subsystem. The timestamp is usually updated every 15 minutes, which means that the timestamp for the SHUTDOWN events will be accurate to within 15 minutes in the event of a power failure. For additional information on shutdown events, refer to PI Server manuals. 

Note: The SHUTDOWN events that are written by the PI Shutdown subsystem are independent of the SHUTDOWN events that are written by the interface when the /stopstat=Shutdown command-line argument is specified.

SHUTDOWN events can be disabled from being written to PI when PI is restarted by setting the Shutdown attribute to 0 for each point. Alternatively, the default behavior of the PI Shutdown Subsystem can be changed to write SHUTDOWN events only for PI points that have their Shutdown attribute set to 0. To change the default behavior, edit the \PI\dat\Shutdown.dat file, as discussed in PI Server manuals.
Bufserv 

It is undesirable to write shutdown events when Bufserv is being used. Bufserv is a utility program that provides the capability to store and forward events to a PI Server, allowing continuous data collection when the Server is down for maintenance, upgrades, backups, and unexpected failures. That is, when PI is shut down, Bufserv will continue to collect data for the interface, making it undesirable to write SHUTDOWN events to the PI points for this interface.

Output Points 
This interface does not support outputs.
Performance Point Configuration

This Interface does not support Performance Points.
I/O Rate Tag Configuration

An I/O Rate tag measures the throughput of an Interface.  In particular, the value of an I/O Rate point represents a 10-minute average of the total number of values per minute that the Interface sends to the PI Server.  Because values are averaged over a 10-minute interval, the first calculated value is not written to the PI Server until 10 minutes after the Interface has started.  The user can configure one I/O Rate tag for each copy of the Interface that is in use. 

Monitoring I/O Rates on the Interface Node

The 10-minute rate averages (in events/minute) can be monitored with a client application such as PI ProcessBook. 

Configuring I/O Rate Tags with PI ICU (Windows)

The PI Interface Configuration Utility (PI ICU) provides a user interface for creating and managing I/O Rate Tags.
[image: image11.png][Input 10Rates Tag:

¥ Enable [0Rates for this interface

A

Cieate

x

Delete

9

Resel

T

| Renane |

i
AddiaFil

Event Courter: [2 Stiggest

Tognae:
Tog Status:
InFi:

Snapshot:

[rismmode PE T

Cieated.

[Yes

[z ey 7 121208)





PI ICU currently allows for one I/O Rate tag to be configured for each copy of the interface that is in use. Some interfaces allow for multiple I/O Rate tags.

Enable IORates for this Interface

The Enable IORates for this interface check box enables or disables the I/O Rate point for the Interface. To disable the I/O Rate point, uncheck this box.  To enable the I/O Rate point, check this box.

Event Counter

The Event Counter number correlates a point specified in the IORates.dat file with this Interface.  This correlation results from the command line parameter

‑ec=x 

where x is the same number that is assigned to the point named in the IORates.dat file.

Tagname

The tag name listed under the Tagname column is the name of the I/O Rates point.

Tag Status

The Tag Status column indicates whether the I/O Rate point currently exists in PI Server. The possible states are:

· Created - This status indicates that the point exists in PI Server

· Not Created - This status indicates that the point does not yet exist in PI Server

· Deleted - This status indicates that the point has just been deleted

· Unknown - This status indicates that the PI ICU is not able to access PI Server

In File

The In File column indicates whether the I/O Rates point listed in the Tagname column and the event counter number listed in the Event Counter column are in the IORates.dat file.  The possible states are:

· Yes - This status indicates that the I/O Rate point and the event counter number are in the IORates.dat file

· No - This status indicates that the I/O Rate point and the event counter number are not in the IORates.dat file

Snapshot

The Snapshot column holds the snapshot value of the I/O Rate tag, if the I/O Rate tag exists in PI. The Snapshot column is updated when the IORates/Status Tags tab is clicked, and when the Interface is first loaded.

Button Menu Options

Create

Create the suggested I/O Rates point with the tag name indicated in the Tagname column.

Delete

Delete the I/O Rate point listed in the Tagname column.

Reset

Change the value in the Tagname text box back to the default value.

Rename

Allow the user to specify a new name for the I/O Rate point listed in the Tagname column.

Add to File

Add the I/O Rate point and the event counter number to the IORates.dat file.

Search [image: image12.bmp]
Allow the user to search the PI Server a previously defined I/O Rate points.

Update Snapshot [image: image13.bmp]
Allow the user to refresh the snapshot value.

Configuring I/O Rate Tags Manually

There are two configuration steps.

1. Configuring the PI Point on the PI Server
2. Configuration on the Interface Node

Configuring PI Point on the PI Server

Create an I/O Rate Tag with the following point attribute values. 

	Attribute

	Value

	PointSource
	L

	PointType
	float32

	Compressing
	0

	ExcDev
	0


Configuration on the Interface Node

For the following examples, assume that the name of the PI tag is PIC37118001, and that the name of the I/O Rate on the home node is PIC37118001.

1. Edit/Create a file called iorates.dat in the PIHOME\dat directory. The PIHOME directory is defined either by the PIPCSHARE entry or the PIHOME entry in the pipc.ini file, which is located in the %windir% directory. If both are specified, the PIPCSHARE entry takes precedence. 

Since the PIHOME directory is typically C:\PIPC, the full name of the iorates.dat file will typically be C:\PIPC\dat\iorates.dat.

Add a line in the iorates.dat file of the form:

PIC37118001, x

where PIC37118001 is the name of the I/O Rate Tag and x corresponds to the first instance of the /ec=x parameter in the startup command file. X can be any number between 2 and 34 or between 51 and 200, inclusive. To specify additional rate counters for additional copies of the interface, create additional I/O Rate tags and additional entries in the iorates.dat file. The event counter, /ec=x, should be unique for each copy of the interface. 

2. Set the /ec=x parameter on the startup command file of the interface to match the event counter in the iorates.dat file.

The interface must be stopped and restarted in order for the I/O Rate tag to take effect. I/O Rates will not be written to the tag until 10 minutes after the interface is started.

Startup Command File

Command-line parameters can begin with a / or with a -. For example, the /ps=M and 
–ps=M command-line parameters are equivalent.

Command file names have a .bat extension. The Windows continuation character (^) allows for the use of multiple lines for the startup command. The maximum length of each line is 1024 characters (1 kilobyte). The number of parameters is unlimited, and the maximum length of each parameter is 1024 characters.

The PI Interface Configuration Utility (PI ICU) provides a tool for configuring the Interface startup command file. 
The PI C37.118 Interface on Windows has a PI ICU Control that will aid in configuring the PI C37.118 Interface startup command file:

Configuring the Interface with PI ICU
Note: PI ICU requires PI 3.3 or greater.

The PI Interface Configuration Utility provides a graphical user interface for configuring PI interfaces. If the interface is configured by the PI ICU, the batch file of the interface (PIC37118.bat) will be maintained by the PI ICU and all configuration changes will be kept in that file and the module database.  The procedure below describes the necessary steps for using PI ICU to configure the PI C37.118 Interface.

From the PI ICU menu, select Interface, then NewWindows Interface Instance from EXE..., and then Browse to the PIC37118.exe executable file.  Then, enter values for Point Source and Interface ID#.  A window such as the following results: 

[image: image14.png]%y Configure a New Interface

Use the Browse butan to select P Intaface service fe e+ to configue. The addiional
parameters shown may akso be selected.

1) Browse to neiface executable (ieqied)

2) Host Pl Server/Cllective fequied):

Bowss,

Path:

MKELLYLAPTOP

3) Optional Setings

Itettace name as displayed in the ICU (optona)

[RELCVLAPTOR

Car1ie -1

Point Saurce:

Intetface ID # Sen

wice ID

Cariie

i Suggest|  [1

Add

Coaioks |0





“Interface name as displayed in the ICU (optional)” will have PI- pre-pended to this name and it will be the display name in the services menu.

Click on Add.  

The following display should appear: 

[image: image15.png]1) C37.118- 1 (PICS71181)is now reacytobe configure it PInerface Cofiguraion Uik

&





Note that in this example the Host PI System is MPKELLYLAPTOP, which means that the interface will be configured to communicate with the local PI Server. However, to configure the interface to communicate with a remote PI Server, select ‘Interface => Connections…’ item from PI ICU menu and make it the default server. If the remote node is not present in the list of servers, it can be added.  

Once the interface is added to PI ICU, near the top of the main PI ICU screen, the Interface Type should be C37118.  If not, use the drop-down box to change the Interface Type to be C37118.

Click on Apply to enable the PI ICU to manage this copy of the PI C37.118 Interface.

[image: image16.png], Pl-Interface Configuration Utility - PIC371181

Interface Tooks Help

IERAS

B R

Intettace: C37.118 1 (PIC371181) > MKELLYLAPTOP

Tipe =
Descrpton
" isf
Vesons:[od
o
Goreral |coorhone
Unine cocopiire

ciect
PISDK | crieak

PIIEEE C37.118

Pl Server Cornestion Status-

Cariie

Unint version 4.3.0.36

0 senerabone

Pl Host Information

MKELLYLAPTOP.
Witeable

carie

Discornested SEME
Debug
Falover
Perfomance Poirts
Perfamance Counters
Healh Pairts

carie

Service

10 Rate

Itetface Status

Intetface ID:

Sean Classes

User [packin

SDK Membe:

API Hostname:

Scan Frequency

Soan Class #

Descipton

Service Urinstalled

PICa7ii81

Port

Intetface Instalaton Path

Type: Nonepicated - PI3

Version Fi343076

D~Froan Fen PP B e . |
=

Not Installed





The next step is to make selections in the interface-specific tab (i.e. “C37118”) that allow the user to enter values for the startup parameters that are particular to the PI C37.118 Interface.  

[image: image17.png], Pl-Interface Configuration Utility - PIC371181
Interface Tools Fielp

NEX|d)> e BRIAIO

Ieiace;  [C37.118-1FICITTT81] > MKELLVLAPTOR B

Tope: cariie ~] PiEEECI7 118 Pl Server Connection Status

Desciion: MKELLYLAPTOP.
Witeable

Vesions:  [FCE TG eeversn 1013 (Gt verson §303

[Gomd - PIIEEE C37.18Inteiface Spesiic Parameters (1013
Unilnt ‘ath to: onfig File:

Service
10 Rate
Itetface Status

’—Aaamana\ Parameters

| Service Uninstalled {PIC371181 - Not Installed




Since the PI C37.118 Interface is a UniInt-based interface, in some cases the user will need to make appropriate selections in the UniInt tab.  This tab allows the user to access UniInt features through the PI ICU and to make changes to the behavior of the interface.  

To set up the interface as a Windows Service, use the Service tab.  This tab allows configuration of the interface to run as a service as well as to starting and stopping of the interface. The interface can also be run interactively from the PI ICU.  To do that go to menu, select the Interface item and then Start Interactive.

For more detailed information on how to use the above-mentioned and other PI ICU tabs and selections, please refer to the PI Interface Configuration Utility User Manual.  The next section describes the selections that are available from the C37118 tab.  Once selections have been made on the PI ICU GUI, press the Apply button in order for PI ICU to make these changes to the interface’s startup file and XML Configuration file.  
The PI C37.118 ICU Control for PI ICU has several sections. A yellow text box indicates that an invalid value has been entered, or that a required value has not been entered
C37118 Interface Tab

Since the startup file of the PI C37.118 Interface is maintained automatically by the PI ICU, use the C37118 tab to configure the startup parameters and not make changes in the file manually.  The following is the description of interface configuration parameters used in the PI ICU Control and corresponding manual parameters.

C37118
[image: image18.png], Pl-Interface Configuration Utility - PIC371181
Interface Tools Fielp

NEX|d)> e BRIAIO

Ieiace;  [C37.118-1FICITTT81] > MKELLVLAPTOR B

Tope: cariie ~] PiEEECI7 118 Pl Server Connection Status

Desciion: MKELLYLAPTOP.
Witeable

Vesions:  [FCE TG eeversn 1013 (Gt verson §303

[Gomd - PIIEEE C37.18Inteiface Spesiic Parameters (1013
Unilnt ‘ath to: onfig File:

Service
10 Rate
Itetface Status

’—Aaamana\ Parameters

| Service Uninstalled {PIC371181 - Not Installed




Path to XML Config File

This box is used to specify the path and filename of the XML Configuration file to be used by the interface.  If there are spaces in the path, then the path and filename should be enclosed in quotation marks. To enter a <UNC Path> click on the … button and choose an existing file from the resulting dialog box (below) or enter a new filename in the File name: text box at the bottom of the screen (/CONFIGFILE=<UNC Path>)
[image: image19.png]Select XML File or enter a File name: below to a create new XML Config File. PIx)

=40

[E2 Configuration Files
[ Example Files

(Spentesto
=i

Spicaniis sa0s.ml
Spicaniis prter_Tcp M.
Spicamis seLszi_Tcram.

9

My Computer

Q@) o e

MyNswerk  Flesofbpe:  [XL Dosuments (o)
Plces

I Open as eadonly






Additional Parameters

This box is used to add any command-line parameters which are not currently supported by the ICU Control.  Each command-line parameter should be separated by a space.  If the argument to a command-line parameter has any embedded space then surround the whole argument in double quotes.

XML Parameters

[image: image20.png], Pl-Interface Configuration Utility - PIC371181

Interface Tooks Help

DX d

B R o

Intettace: Carie

1 (PIC371181) > MKELLYLAPTOR

Tope: cariie

~] PlEEECa7118

Descipton

Versions: FIC37118 2% version 1.01.3

General

Unint
PISDK
Discornested Statup
Debug
Falover
Perfomance Poirts
Perfamance Counters
Healh Pairts

carie

Service

10 Rate

Itetface Status

i verson 43038

FIIEEE C37.118 Interace-Specific Parameters 1.0.1.3)

Pl Server Cornestion Status-
MKELLYLAPTOP.
Witeable

Path to XML Config File: [D:\Program Fies\PIPCInterfaces\C37118VPIC37118.ml

Devce Confiraton e Setings
Session Corfiursion
Sesson Wi 10 Tineout
Syne Err Ackon
Data Soting Acton
DataVaidAcion
PMU Eror Acion

Leap Second Action

Addiional Patameters

Yes

Mark a5 Questonable

Mark a5 Questonable

Discard the Data

Discard the Data

Store the Valie

Service Urinstalled PIC371181 - NotInstalled





Session

The session section contains configuration parameters which control the behavior of the interface when various error conditions occur.

The following illustrates the Session section of the C37.118 ICU.

[image: image21.png]‘Session Configuration’

Wite [0 Timeout ~ [res =

ScEnoréction [Maik as Questonable |
DataSotingActon [Maik as Questonable |
DataValdActon [DicadtheData <]
PMUEroiActon  [DicadtheData <]
LespSecondAction [Starethevae <]




· Write IO Timeout – If set to yes, the interface will write the system digital state of I/O Timeout when no C37.118 data messages are received within the timeframe specified in the LocalEndPoint section. (WriteIOTimeout=#, Default: 1 (Yes), Range:0-1)
· Sync Error Action – Controls the behavior of the interface when the SYNC flag is set in the C37.118 data stream. (SyncErrorAction=#, Default: 1 (Mark as Questionable), Range 0-3)

· Data Sorting Action – Controls the behavior of the interface when the Data Sorting flag is set in the C37.118 data stream. This flag is set on in a PDC data stream when a PMU loses time synchronization making it impossible for the PDC to time correlate the phasor data. (DataSortingAction=#, Default: 1 (Mark as Questionable), Range 0-3)

· Data Valid Action – Controls the behavior of the interface when the Data Valid flag is set in the C37.118 data stream. This flag is set in a PDC data stream when the PDC loses connection to a PMU. When this happens, the PDC typically zero fills the data. (DataValidAction=#, Default: 3 (Disard the Data), Range 0-3)

· PMU Error Action – Controls the behavior of the interface when the PMU Error flag is set in the C37.118 data stream. This flag is set when an error occurs on a PMU and indicates a possible error in the data. (PMUErrorAction=#, Default: 3 (Disard the Data), Range 0-3)

· Leap Second Action – Controls the behavior of the interface when the Leap Second flag is set in the C37.118 data stream. This flag indicates that a leap second has occurred. (LeapSecondAction=#, Default: 0 (Store the Value), Range 0-3)

The available selections for Sync Error, Data Sorting, Data Valid, PMU Error and Leap Second Actions above are as follows.

· 0 (Store the Value) – The interface will store the value normally.

· 1 (Mark as Questionable) – The interface will store the value but mark it as questionable.

· 2 (Store the Corresponding System Digital State) – The interface will store the corresponding system state. 

· 3 (Discard the Data) – The interface will not store the value in PI.
LocalEndPoint

[image: image22.png], Pl-Interface Configuration Utility - PIC371181
Interface Tools Fielp

DX d B R @

Intettace: C37.118 1 (PIC371181) > MKELLYLAPTOP

Tope: cariie ] PlEEEC37118 Pl Server Cornestion Status-

Desciion: MKELLYLAPTOP.
Witeable

Vesiors:  [FCaTT B verdon 013 [l veson 430%

[Gemesl - PIIEEE C37.118 Inteface-Specific Parameters (1.0.1.3)

Unint ® [
ath o XML Confg Fik: rogram Fils\PIPCAntafaces\ L7 1VPICAT1 T
Yok io [D:\Program Files\PIPCAIntertaces\C371 1BVPICS7T1B.am.

Discornected Startup ||~ Device Configuiation fle Settings

Debus - [ —
Falover Llmlal] e o

Enabled [os <

Perfomance Poirts Session —
Perfamance Counters EndFornl eeniiee: | Tl CommDLL

Heallh Pairs RecomectAate [30000 ms [
cariie =l

Service
10 Rate
Itetface Status

Addiional Patameters

Service Urinstalled PIC371181 - NotInstalled




The LocalEndPoint section defines parameters specific to the interface side of a PDC / PMU connection.

The following illustrates the format of the LocalEndPoint section of the C37.118 ICU.

[image: image23.png]Local End Paint Configuration

cE o[ Enabed
robled [72:
© Sl Ty
Dat Tineout [1000 e CommpUL

RecomectRate P00 ms [ |





· IP – Identifies this LocalEndPoint as using a TCP connection (Type=<string>, Range: IP or Serial)

· Serial - Identifies this LocalEndPoint as using a Serial connection (Type=<string>, Range: IP or Serial)
· Id - Specifies the numeric Id of the LocalEndPoint. The Id uniquely identifies the LocalEndPoint when configuring tags for an interface. The Id must be unique among all LocalEndPoints. (Id=#, Default:None, Range: 0-32767, Required)

· Enabled – Allows the LocalEndPoint and everything associated with it to be disabled and not loaded by the interface. It can then be re-enabled with having to reconfigure. (Enabled=#, Default: 1 (Yes), Range: 0-1)

· Data Timeout - Controls the length of time to wait, in milliseconds, for data responses. The recommended value is 5 times the configured PMU data rate. (DataTimeout=#, Default:1000, Range: 10-65,535)

· Reconnect Rate – Controls the rate in which the interface attempts to re-establish communications with the PDC / PMU. (ReconnectRate=#, Default:30000, Range: 10-65,535)

· Comm Dll – Defines the Communications Plug-In to be used to communicate with the PDC / PMU. Due to the variation in application level functionality from one device vendor to another, the plug-in approach allows for new devices to be easily supported. Refer to the Communications Plug-In appendix in this manual or to the OSIsoft support site for details on available plug-in’s.

IP Configuration

The following controls are available when Type=”IP” is selected.

[image: image24.png]IP Configuration
Frotocol Pott  Close Command Sacket [Yes v

Cnd [TP =] cma [0 ™ Use Mulicast P Ad
Data [UDP v Data [0 2= o o




· Command Protocol - Specifies the protocol to use for C37.118 Command and Configuration messages. (CommandProtocol=<type>, Default: TCP, Range: TCP or UDP)
· Local Command Port – Specifies the local port to listen on for configuration packets. If not specified the interface will not specify a specific port (system assigned). This parameter will typically be used when the command protocol is UDP in order to facilitate configuration with firewalls. If this value is specified it must be different than the Local Data Port value. (LocalCommandPort=#, Default: 0 (System Assigned), Range: 1024-65,535)

· Data Protocol - Specifies the protocol to use for C37.118 data messages. (DataProtocol=<type>, Default: UDP, Range: TCP or UDP)
· Local Data Port – Specifies the local port to listen on for data packets. If not specified the interface will not specify a specific port (system assigned). This parameter will typically be used when the data protocol is UDP in order to facilitate configuration with firewalls. For some PDC / PMU configurations in which the device is sends to a predefined data port, this value will also need to be specified. It is also required if Multicast being used. (LocalDataPort=#, Default: 0 (System Assigned), Range: 1024-65,535)

· Close Command Socket – If Yes is specified, the interface will close the command socket (if different than the data socket) once a command is sent and the expected response is successfully received. Some devices, such as the Arbiter 1133, expect that the command socket be closed after use. Others, such as SEL devices require the socket remain open. (CloseCommandSocket=#, Default: 1 (Yes), Range: 0 (No) – 1 (Yes))
· Use Multicast IP Addr - This parameter is valid only when the Local Data Protocol is specified as UDP. When specified, the interface will be configured to listen for C37.118 data messages via Multicast. (MulticastIPAddress=<ipaddr>, Default: None)

Serial Configuration

The following controls are available when Type=”Serial” is selected.
[image: image25.png]Serial Configuration

Baud COM Pt Pay Stop Bis

fom =l [ e s [ =





· Baud – Specifies speed at which to communicate with the PDC / PMU. Refer to your PDC / PMU hardware users guide for supported baud rates. (Baud=#, Default: 38400, Range: 300-115200)
· COM Port - The numeric value of the serial COM port to use.  For example if using COM1 set this value to 1. (Port=#, Range: 1-Max Ports)

· Parity – Specifies the error checking parity to use. (Parity=#, Default: 0 (NONE), Values: 0 (NONE), 1 (ODD), 2 (EVEN), 3 (MARK), and 4 (SPACE))
· Stop Bits – Specifies the number of stop bits following a message. (StopBits=#, Default: 0 (1 bit), Values: 0 (1 bit), 1 (2 bits), 2 (1.5 bits))
RemoteEndPoint

The RemoteEndPoint represents the remote (PDC / PMU side) of a physical connection. Each RemoteEndPoint node will have one or more PMU child nodes.  Each of the PMU nodes will represent a PMU that the PI C37.118 interface will communicate with through the physical port described by the LocalEndPoint / RemoteEndPoint child node pair.
RemoteEndPoint Child Nodes that apply to all connection types.


· Id Code - Specifies the numeric Id of the PDC or PMU. This must match the IDCODE field sent by the C37.118 device. If the device is a PDC it is important to note that this must match the IDCODE of the PDC and not the PMU(s) being serviced by the PDC. (IdCode=#, Range: 0-32,767)

· Description - User defined description of the RemoteEndPoint. Ie. “Substation xyz”. This attribute is used by the interface when logging messages regarding the RemoteEndPoint. (Description=<string>)

The following illustrates the RemoteEndPoint section for an IP LocalEndPoint.

[image: image26.png]FRemote End Point Configuration

S e

Desciption

Remate Crd Part [4713

& Host Name

1P Address

e





· Remote Data Port – Specifies the remote (PDC) port to be used for data packets. If not specified the interface will assume a specific port (system assigned). If this field is specified, the data being received from the PDC / PMU must originate from this port. Most PDCs and PMUs use a random system assigned port. (RemoteDataPort=#, Default: 4712, Range: 1024-65,535)
· Remote Command Port – Specifies the remote port to use for command and configuration packets. The interface will send CONFIG1, CONFIG2 and HEADER request commands to this port. (RemoteCommandPort=#, Default: 4713, Range: 1024-65,535)
· Host Name – If this control is selected the PDC / PMU addressing information is passed by host name.(HostName=<nodename> or <IPAddr>) 

· IP Address – If this control is selected the PDC / PMU addressing information is passed as an IP address in dotted decimal notation. (HostName=<nodename> or <IPAddr>)
The following illustrates the RemoteEndPoint section for a Serial LocalEndPoint.

[image: image27.png]Remote End Point Configuration-
ot [

Desciption





PMU

The PMU section describes the characteristics of each PMU. If the RemoteEndPoint is a PDC then there may be multiple PMUs, otherwise there should be only one PMU child node per RemoteEndPoint.

[image: image28.png]PMU Configuration





· Id Code - Specifies the numeric Id of the PMU. This must match the IDCODE field sent by the C37.118 device. If there are multiple PMU nodes associated with a RemoteEndPoint (RemoteEndPoint is a PDC) with it this Id must be unique within the RemoteEndPoint collection and should match the PMUs IDCODE and not the IDCODE of the PDC itself. (IdCode=#, Range: 0-32,767)

· Latitude - Specifies the geographic latitude of the PMU. This field is optional. However, if the latitude is specified, then the longitude must also be specified, otherwise the interface will log an error and exit. If no sign is specified then + is assumed. (Latitude=+/-#.#, Range: -90.0 to +90.0)

· Longitude - Specifies the geographic longitude of the PMU. This field is optional. However, if the longitude is specified, then the latitude must also be specified, otherwise the interface will log an error and exit. If no sign is specified then + is assumed. (Longitude=+/-#.#, Range: -180.0 to +180.0)

PIC37118 XML Nodes, Elements, and Attributes

There are four major nodes that must be included in the PI C37.118 XML configuration file.  The nodes are the Root, LocalEndPoint, RemoteEndPoint and PMU nodes.
Note: An Interface Configuration Utility (ICU) Plug-In is available for the PI C37.118 Interface to assist in creating the XML configuration file. OSIsoft strongly suggests the use of the ICU.
Root Node

The root node must be named PI_C37_118.Session and contains one or more LocalEndPoint leaf nodes.
	PI_C37118.Session Child Nodes
	Description

	Example:  <PI_C37_118.Session”>

	WriteIOTimeout

Optional

XMLType: Attribute

Default: 1
	By default, the interface will write the digital state I/O Timeout to all measurement type tags when a communications timeout condition is encountered. Setting the WriteIOTimeout attribute to a value of 0 will cause the interface to suppress writing I/O Timeout to the measurement tags.

Valid values for this attribute are 0 (No) to not write I/O Timeout or 1 (Yes) to write I/O Timeout. 

	PMUErrorAction

Optional

XMLType: Attribute

Default: 3
	The PMUErrorAction attribute controls the behavior of the interface when the PMU Error flag is detected in the STAT word of the message. This flag indicates that there is a problem with the PMU hardware and that the data may not be valid. 

The default behavior of the interface is to discard the data.

Valid selections for this attribute are:

0 – Store the value normally (Not recommended)

1 – Mark the data as questionable. 

2 – Stores the PMU Error system digital state for all measurement values.

3 - Discards the data.

	DataValidAction

Optional

XMLType: Attribute

Default: 3
	The DataValidAction attribute controls the behavior of the interface when the Data Invalid flag is detected in the STAT word of the message. This flag indicates that there is a problem with the data for the PMU may not be valid. This flag is typically set when the data stream is coming from a PDC versus a single PMU and is usually due to the PDC not receiving a data frame from the PMU in a reasonable time. The PDC typically blank fills the data. 

The default behavior of the interface is to discard the data.

Valid selections for this attribute are:

0 – Store the value normally (Not recommended)

1 – Mark the data as questionable. 

2 – Stores the PMU Error system digital state for all measurement values

3 – Discards the data.

	SyncErrorAction

Optional

XMLType: Attribute

Default: 1
	The SyncErrorAction attribute controls the behavior of the interface when the PMU Sync Error flag is detected in the STAT word of the message. This flag indicates that there is a problem with the time synchronization of the PMU and that the quality of the timestamp is other than normal. 

The default behavior of the interface is to mark the data as questionable.

Valid selections for this attribute are:

0 – Store the value normally (Not recommended)

1 – Mark the data as questionable. 

2 – Stores the PMU Error system digital state for all measurement values.

3 - Discards the data.



	DataSortingAction

Optional

XMLType: Attribute

Default: 1
	The DataSortingAction attribute controls the behavior of the interface when the Data Sorting flag is detected in the STAT word of the message. This error should only occur if the data stream is coming from a PDC. This flag indicates that the data for the PMU is being integrated into the data frame by arrival and not timestamp. 

The default behavior of the interface is to mark the data as questionable.

Valid selections for this attribute are:

0 – Store the value normally (Not recommended)

1 – Mark the data as questionable. 

2 – Stores the PMU Error system digital state for all measurement values.

3 - Discards the data.



	LeapSecondAction

Optional

XMLType: Attribute

Default: 0
	The LeapSecondAction attribute controls the behavior of the interface when one of the leap second flags is detected in the STAT word of the message. This occurs when a leapsecond is occurring. 

The default behavior of the interface is to store the data normally.

Valid selections for this attribute are:

0 – Store the value normally

1 – Mark the data as questionable. 

2 – Stores the PMU Error system digital state for all measurement values.

3 - Discards the data.




LocalEndPoint Nodes

Child nodes of the root node are LocalEndPoint nodes.  The LocalEndPoint nodes are used to specify the properties of the local (interface side) of a physical connection such as a communication port, or TCP port.  The Type attribute must be either Serial or IP.  The child nodes will depend on the value of the Type attribute.  A serial communications port will have different child nodes than an IP port. There can only be one RemoteEndPoint Node for each LocalEndPoint Node. 

	LocalEndPoint Child Nodes that apply to all connection types.
	Description

	Example:  <RemoteEndPoint> 
	

	Type

Required

XML Type: Element

Default: None
	Specifies the communications type. Values are “IP” or “Serial”

	Id

Required

XMLType: Attribute

Default: None
	Specifies the numeric Id of the LocalEndPoint. The Id uniquely identifies the LocalEndPoint when configuring tags for an interface. The Id must be unique among all LocalEndPoints for an interface.

Valid ranges: {0-32767}

	Enabled

Optional

XML Type: Attribute

Default: 1
	Enabled – Allows the LocalEndPoint and everything associated with it to be disabled and not loaded by the interface. It can then be re-enabled with having to reconfigure.  A value of 0 (No) indicates that the LocalEndPoint is disabled. A value of 1 (Yes) indicates it is enabled.


	CommDll

Required

XMLType: Element

Default: None
	Defines the Communications Plug-In to be used to communicate with the PDC / PMU. Due to the variation in application level functionality from one device vendor to another, the plug-in approach allows for new devices to be easily supported. Refer to the Communications Plug-In appendix in this manual or to the OSIsoft support site for details on available plug-in’s.

	DataTimeout

Optional

XMLType: Attribute

Default: 1000 


(1 second)
	Controls the length of time to wait, in milliseconds, for data responses.

Valid range: { 10-65535}



	ReconnectRate

Optional

XMLType: Attribute

Default: 30000 


(30 seconds)
	Controls the interval, in milliseconds, to be used when attempting to restart communications with a C37.118 device.

Valid Range: {10-65535}




	LocalEndPoint Child Nodes for Type=”Serial”
	Description

	Example:  <LocalEndPoint Type=”Serial”>

	Port

Required
XMLType: Attribute

Default: None
	The numeric value of the serial COM port to use.  For example if using COM1 set this value to 1. 
Valid range: {1 – Max Ports}

	Baud

Optional
XMLType: Attribute

Default: 38400
	The speed at which to communicate. 

Valid range: {Refer to your PDC / PMU hardware users guide for supported baud rates.}

	Parity

Optional
XMLType: Attribute

Default: None
	The error checking parity to use.  This can be 0 for NONE, 1 for ODD, 2 for EVEN, 3 for MARK, and 4 for SPACE.  

Valid range: {0,1,2,3,4}

	StopBits

Optional
XMLType: Attribute

Default: None
	The number of stop bits following a message.  This can be 0 for one, 1 for two, or 2 for one and a half stop bits.  

Valid range: {0,1,2}


	LocalEndPoint Child Nodes for Type=”IP”
	Description

	Example:  <LocalEndPoint Type=”IP”>

	
	

	DataProtocol

Optional

XMLType: Element

Default: UDP
	Specifies the protocol to use for C37.118 data messages.

Valid Values: {UDP or TCP}



	LocalDataPort

Required if Multicast being used, otherwise optional

XMLType: Attribute

Default: 0
      (System Assigned)
	The local port to bind to for data packets. If not specified or zero the interface will not specify a specific port (system assigned). This parameter will typically be used when the data protocol is UDP in order to facilitate configuration with firewalls. If this value is specified it must be different than the LocalCommandPort value or zero.
Valid range: {1024-65535}

	MulticastIPAddress

Optional

XMLType: Element

Default: None
	This parameter is valid only when the DataProtocol is specified as UDP. When specified, the interface will be configured to listen for C37.118 data messages via Multicast.

Valid values: {224.0.0.1-224.255.255.254}



	CommandProtocol

Optional

XMLType: Element

Default: TCP
	Specifies the protocol to use for C37.118 Command and Configuration messages. If this node is not specified, the interface will use the protocol specified by the DataProtocol node or the default DataProtocol if it is not specified.

Valid Values: {UDP or TCP}

	LocalCommandPort

Optional

XMLType: Attribute

Default: 0
     (System  Assigned)


	The local port to bind to for configuration packets. If not specified or zero  the interface will not specify a specific port (system assigned). This parameter will typically be used when the data protocol is UDP in order to facilitate configuration with firewalls. If this value is specified it must be different than the LocalDataPort value or zero.

Valid range: {1024-65535}

	CloseCommandSocket

Optional

XML Type: Attribute

Default Value: 1
	Some PMU / PDC models require the socket used for sending commands and receiving configuration and header responses be closed after use, while others require that they remain open. The Arbiter 1133 for example, requires that the socket be closed. All SEL PMU and PDC models require the socket remain open.

This option only effects configurations in which the command/command response is on a separate protocol and/or port from the C37.118 data stream.

Valid Values: 0 ( Leave Open) or 1 (Close After Use)


RemoteEndPoint Nodes

The RemoteEndPoint node is child node of the LocalEndPoint node(s). The RemoteEndPoint node represents the remote (PDC / PMU side) of a physical connection. The RemoteEndPoint node will have one or more PMU child nodes.  Each of the PMU nodes will represent a PMU that the PI C37.118 interface will communicate with through the physical port described by the LocalEndPoint / RemoteEndPoint child node pair.
	RemoteEndPoint Child Nodes that apply to all connection types.
	Description

	Example:  <RemoteEndPoint> 
	

	IdCode

Required

XMLType: Attribute

Default: None
	Specifies the numeric Id of the PDC or PMU. This must match the IDCODE field sent by the C37.118 device. If a LocalEndPoint has multiple RemoteEndPoint nodes associated with it this Id must be unique within the LocalEndPoint collection.

Valid ranges: {0-32767}

	Description

Optional

XML Type: Element

Default: None
	User defined description of the RemoteEndPoint. Ie. “Substation xyz”. This attribute is used by the interface when logging messages regarding the RemoteEndPoint.


	RemoteEndPoint Child Nodes when LocalEndPoint is “Serial”
	Description

	Example:  <RemoteEndPoint> 
	

	
	There are no Serial specific RemoteEndPoint child nodes


	RemoteEndPoint Child Nodes when LocalEndPoint is “IP”
	Description

	Example:  <RemoteEndPoint> 
	

	HostName

Required

XMLType: Element

Default: None
	The Host name or IP address of the PDC or PMU. If using the PIC37118_Comm003.DLL, the supplied name should be set to 127.0.0.1 to indicate the interface will listen on the specified LocalDataPort for incoming C37.118 messages.
Valid range: {Any valid address or name}

Example: 

<Hostname> 192.164.55.128</Hostname> or

<Hostname> myhost </Hostname> 

	RemoteDataPort

Optional

XMLType: Attribute

Default: 4712
	The remote port to be used for data packets. If not specified the interface will not specify a specific port (system assigned). 

Valid range: {1024-65535} or 0 (System Assigned)

	RemoteCommandPort

Optional

XMLType: Attribute

Default: 4713
	The remote port to use for command configuration packets. 

Valid range: {1024-65535}


PMU Child Nodes

PMU nodes are child nodes of the RemoteEndPoint nodes. The PMU node describes the characteristics of the PMU. If the RemoteEndPoint is a PDC then there may be multiple PMUs, otherwise there should be only one PMU child node per RemoteEndPoint.
	PMU Child Nodes
	Description

	Example:  <PMU> 
	

	IdCode

Required

XMLType: Attribute

Default: None
	Specifies the numeric Id of the PMU. This must match the IDCODE field sent by the C37.118 device. If there are multiple PMU nodes associated with a RemoteEndPoint (RemoteEndPoint is a PDC) with it this Id must be unique within the RemoteEndPoint collection and should match the PMUs IDCODE and not the PDCs. 

Valid ranges: {0-32767}

	Latitude

Optional

XMLType: Attribute
Default: None
	Specifies the geographic latitude of the PMU. If the latitude is specified, then the longitude must also be specified Otherwise the interface will log an error and exit.

Valid range: {-90.0 to +90.0}



	Longitude

Optional

XMLType: Attribute
Default: None
	Specifies the geographic longitude of the PMU. If the latitude is specified, then the longitude must also be specified Otherwise the interface will log an error and exit.

Valid range: {-180.0 to +180.0}




Sample PIC37118.xml File

<?xml version="1.0"?>

<PI_C37_118.Session WriteIOTimeout="1" DataSortingAction="1" PMUErrorAction="3" SyncErrorAction="1" DataValidAction="3" LeapSecondAction="0">


<LocalEndPoint Id="1" LocalDataPort="1024" LocalCommandPort="1025" DataTimeout="1000">



<Type>IP</Type>



<CommDLL>PIC37118_Comm001.dll</CommDLL>



<CommandProtocol>TCP</CommandProtocol>



<DataProtocol>UDP</DataProtocol>



<MulticastIPAddress>239.254.1.2</MulticastIPAddress>




<RemoteEndPoint IdCode="1">





<Description>Arbiter in Savannah</Description>





<HostName>gap001</HostName>






<PMU IdCode="1" Latitude="37.127652" Longitude="-122.876365"/>






<PMU IdCode="2"/>




</RemoteEndPoint>


</LocalEndPoint>

</PI_C37_118.Session>

Command-line Parameters
	Parameter
	Description

	/configfile=<UNC Path>
Optional


	This parameter specifies the interface configuration file to use to define the C37.118 device that the interface will communicate with.

	/ec=#
Optional
	The first instance of the /ec parameter on the command-line is used to specify a counter number, #, for an I/O Rate point. If # is not specified, then the default event counter is 1. Also, if the /ec parameter is not specified at all, there is still a default event counter of 1 associated with the interface. If there is an I/O Rate point that is associated with an event counter of 1, each copy of the interface that is running without /ec=# explicitly defined will write to the same I/O Rate point. This means either explicitly defining an event counter other than 1 for each copy of the interface or not associating any I/O Rate points with event counter 1. Configuration of I/O Rate points is discussed in the section called “I/O Rate Tag Configuration.”

	/host=host:port
Required 


	The /host parameter is used to specify the PI Home node.  Host is the IP address of the PI Sever node or the domain name of the PI Server node.  Port is the port number for TCP/IP communication. The port is always 5450. It is recommended to explicitly define the host and port on the command-line with the /host parameter. Nevertheless, if either the host or port is not specified, the interface will attempt to use defaults. 

Examples:
The interface is running on a PI Interface Node, the domain name of the PI home node is Marvin, and the IP address of Marvin is 206.79.198.30. Valid /host parameters would be:
/host=marvin                      
/host=marvin:5450 
/host=206.79.198.30
/host=206.79.198.30:5450

	/id=x

Highly Recommended
	The /id parameter is used to specify the interface identifier. 

The interface identifier is a string that is no longer than 9 characters in length. UniInt concatenates this string to the header that is used to identify error messages as belonging to a particular interface. See the section called Appendix A: Error and Informational Messages for more information.

UniInt always uses the /id parameter in the fashion described above. This interface also uses the /id parameter to identify a particular interface copy number that corresponds to an integer value that is assigned to Location1 attribute. For this interface, use only numeric characters in the identifier. For example,

/id=1

	/ps=c…
Required
	The /ps parameter specifies the point source for the interface. X is not case sensitive and can be any unique single or multiple character string. For example, /ps=P and /ps=p are equivalent. 

The point source that is assigned with the /ps parameter corresponds to the PointSource attribute of individual PI Points. The interface will attempt to load only those PI points with the appropriate point source. 

	/q

Optional


	When the /q parameter is present, Snapshots and exceptions are queued before they are sent to the PI Server node. 

Note: Due to the data rates typically associated with C37.118 devices, this interface requires the use of the /q option.
Extended PI API mode behavior:

The maximum queue size is close to 4000 bytes. The queue is flushed between scans if it is not filled.

Non-Extended PI API mode behavior:

The maximum queue size is 255 bytes for a PI Interface node. For example, if the interface is running on a UNIX node and is communicating to a PI  Server, then the maximum queue size is 255. The queue is flushed between scans if it is not filled.

When the /q parameter is specified in non-extended PI API mode, the PI API sends integer values as 16-bit integers instead of 32-bit integers. Therefore, integer points will be limited to values between 0 and 32767. Values higher than 32767 need to be sent to floating-point PI tags.

	/stopstat
or
/stopstat=
digstate
Default:
/stopstat=
”Intf Shut”
Optional
	If the /stopstat parameter is present on the startup command line, then the digital state Intf Shut will be written to each PI Point when the interface is stopped. 

If /stopstat=digstate is present on the command line, then the digital state, digstate, will be written to each PI Point when the interface is stopped. For a PI 3 Server, digstate must be in the system digital state table. 
If neither /stopstat nor /stopstat=digstate is specified on the command line, then no digital states will be written when the interface is shut down.

Examples:
/stopstat=shutdown
/stopstat=”Intf Shut”            

The entire digstate value should be enclosed within double quotes when there is a space in digstate.

	/TagConfig=xxx

Optional
	The /TagConfig parameter can be used to assist in creating PI tags. Since the C37.118 specification doesn’t dictate the names to use for Phasor, Analog and Digital channels, PMU vendors use different names.  
This command-line parameter can be temporarily specified in the Additional Parameters test box in the ICU when initially configuring the interface. When the interface is started it will read the CONFIG2 block from the PDC / PMU and output a comma delimited file that has the various PI point attributes filled in. The file can then be edited as needed and then imported into PI via SMT.
Since the interface will exit after the file is dumped, it is important to remove this command-line parameter for normal operation. 


Sample PIC37118.bat File

The following is an example file:

REM=======================================================================
REM

REM
PIC37118.bat

REM

REM Sample startup file for the PI IEEE C37.118 Interface to the PI System

REM

REM=======================================================================
REM 

REM OSIsoft strongly recommends using PI ICU to modify startup files.

REM

REM Sample command line

REM

    .\PIC37118.exe ^
    /configfile="E:\Program Files\PIPC\Interfaces\C37118\PIC37118.xml" ^
    /ps=C37118 /ID=1 /host=XXXXXX:5450 /ec=2 /maxstoptime=120 /perf=8 

REM

REM End of pic37118.bat File
Interface Node Clock

Windows 
Make sure that the time and time zone settings on the computer are correct.  To confirm, run the Date/Time applet located in the Windows Control Panel.  If the locale where the interface node resides observes Daylight Saving Time, check the box marked “Automatically adjust clock for daylight saving changes”.  For example,

[image: image29.png]Date and Time Properties

Date & Time | Time

[t6M1-08:00) Pocic Time (U5 & Canada); Tiuens v

kfor daylight saving





In addition, make sure that the TZ environment variable is not defined.  All of the currently defined environment variables can be viewed by opening a Command Prompt window and typing set.  That is,

C:> set

Make sure that the TZ environment variable is not defined. All of the currently defined environment variables can be viewed by opening a Command Prompt window and typing set. Confirm that TZ is not in the resulting list.  If it is, run the System applet of the Control Panel, click the Environment tab, and remove TZ from the list of environment variables.

Security

Windows
The PI Firewall Database and the PI Proxy Database must be configured so that the interface is allowed to write data to the PI Server. See “Modifying the Firewall Database” and “Modifying the Proxy Database” in the PI Server manuals.

Note that the Trust Database, which is maintained by the Base Subsystem, replaces the Proxy Database used prior to PI version 3.3. The Trust Database maintains all the functionality of the proxy mechanism while being more secure.
See “Trust Login Security” in the chapter “PI System Management” of the PI Universal Data Server System Management Guide.

If the interface cannot write data to the PI Server because it has insufficient privileges, a –10401 error will be reported in the pipc.log file. If the interface cannot send data to a PI2 Serve, it writes a –999 error. See the section “Appendix A: Error and Informational Messages” for additional information on error messaging.

PI Server v3.3 and Higher

Security configuration using piconfig

For PI Server v3.3 and higher, the following example demonstrates how to edit the PI Trust table:

C:\PI\adm> piconfig

@table pitrust

@mode create

@istr Trust,IPAddr,NetMask,PIUser

a_trust_name,192.168.100.11,255.255.255.255,piadmin

@quit

For the above,

Trust: An arbitrary name for the trust table entry; in the above example,

a_trust_name
IPAddr: the IP Address of the computer running the Interface; in the above example,

192.168.100.11
NetMask: the network mask; 255.255.255.255 specifies an exact match with IPAddr
PIUser:  the PI user the Interface to be entrusted as; piadmin is usually an appropriate user

Security Configuring using Trust Editor

The Trust Editor plug-in for PI System Management Tools 3.x may also be used to edit the PI Trust table.

See the PI System Management chapter in the PI Server manual for more details on security configuration.

PI Server v3.2

For PI Server v3.2, the following example demonstrates how to edit the PI Proxy table:

C:\PI\adm> piconfig

@table pi_gen,piproxy

@mode create

@istr host,proxyaccount

piapimachine,piadmin

@quit

In place of piapimachine, put the name of the PI Interface node as it is seen by PI Server.

Starting / Stopping the Interface on Windows 
This section describes starting and stopping the interface once it has been installed as a service. See the UniInt Interface User Manual to run the interface interactively.

[image: image30.png]



Starting Interface as a Service

If the interface was installed a service, it can be started from PI ICU, the services control panel or with the command:

PIC37118.exe –start

To start the interface service with PI ICU, use the [image: image31.png]


 button on the PI ICU toolbar.

A message will inform the user of the the status of the interface service. Even if the message indicates that the service has started successfully, double check through the Services control panel applet. Services may terminate immediately after startup for a variety of reasons, and one typical reason is that the service is not able to find the command-line parameters in the associated .bat file. Verify that the root name of the .bat file and the .exe file are the same, and that the .bat file and the .exe file are in the same directory. Further troubleshooting of services might require consulting the pipc.log file, Windows Event Viewer, or other sources of log messages. See the section “Appendix A: Error and Informational Messages,” for additional information.
Stopping Interface Running as a Service

If the interface was installed a service, it can be stopped at any time from PI ICU, the services control panel or with the command:

PIC37118.exe –stop

The service can be removed by:

PIC37118.exe –remove

To stop the interface service with PI ICU, use the [image: image32.png]


 button on the PI ICU toolbar.

Buffering

Buffering refers to an Interface Node’s ability to temporarily store the data that interfaces collect and to forward these data to the appropriate PI Servers. OSIsoft strongly recommends that you enable buffering on your Interface Nodes. Otherwise, if the Interface Node stops communicating with the PI Server, you lose the data that your interfaces collect. 

The PI SDK installation kit installs two buffering applications: the PI Buffer Subsystem (PIBufss) and the PI API Buffer Server (Bufserv).  PIBufss and Bufserv are mutually exclusive; that is, on a particular computer, you can run only one of them at any given time. 

If you have PI Servers that are part of a PI Collective, PIBufss supports n-way buffering. N-way buffering refers to the ability of a buffering application to send the same data to each of the PI Servers in a PI Collective. (Bufserv also supports n-way buffering, but OSIsoft recommends that you run PIBufss instead.)

Which Buffering Application to Use

You should use PIBufss whenever possible because it offers better throughput than Bufserv. In addition, if the interfaces on an Interface Node are sending data to a PI Collective, PIBufss guarantees identical data in the archive records of all the PI Servers that are part of that collective. 

You can use PIBufss only under the following conditions:

· the PI Server version is at least 3.4.375.x; and

· all of the interfaces running on the Interface Node send data to the same PI Server or to the same PI Collective.

If any of the following scenarios apply, you must use Bufserv:

· the PI Server version is earlier than 3.4.375.x; or

· the Interface node runs multiple interfaces, and these interfaces send data to multiple PI Servers that are not part of a single PI Collective. 

If an Interface Node runs multiple interfaces, and these interfaces send data to two or more PI Collectives, then neither PIBufss nor Bufserv is appropriate. The reason is that PIBufss and Bufserv can buffer data only to a single collective. If you need to buffer to more than one PI Collective, you need to use two or more Interface Nodes to run your interfaces.

It is technically possible to run Bufserv on the PI Server Node. However, OSIsoft does not recommend this configuration.

How Buffering Works

A complete technical description of PIBufss and Bufserv is beyond the scope of this document. However, the following paragraphs provide some insights on how buffering works.

When an Interface Node has Buffering enabled, the buffering application (PIBufss or Bufserv) connects to the PI Server. It also creates shared memory storage.

When an interface program makes a PI API function call that writes data to the PI Server (for example, pisn_sendexceptionqx()), the PI API checks whether buffering is enabled. If it is, these data writing functions do not send the interface data to the PI Server. Instead, they write the data to the shared memory storage that the buffering application created. 

The buffering application (either Bufserv or PIBufss) in turn

· reads the data in shared memory, and

· if a connection to the PI Server exists, sends the data to the PI Server; or

· if there is no connection to the PI Server, continues to store the data in shared memory (if shared memory storage is available) or writes the data to disk (if shared memory storage is full).

When the buffering application re-establishes connection to the PI Server, it writes to the PI Server the interface data contained in both shared memory storage and disk.

(Before sending data to the PI Server, PIBufss performs further tasks such data validation and data compression, but the description of these tasks is beyond the scope of this document.)

When PIBufss writes interface data to disk, it writes to multiple files. The names of these buffering files are PIBUFQ_*.DAT. 

When Bufserv writes interface data to disk, it writes to a single file. The name of its buffering file is APIBUF.DAT. 

As a previous paragraph indicates, PIBufss and Bufserv create shared memory storage at startup. These memory buffers must be large enough to accommodate the data that an interface collects during a single scan. Otherwise, the interface may fail to write all its collected data to the memory buffers, resulting in data loss. The buffering configuration section of this chapter provides guidelines for sizing these memory buffers.

When buffering is enabled, it affects the entire Interface Node. That is, you do not have a scenario whereby the buffering application buffers data for one interface running on an Interface Node but not for another interface running on the same Interface Node.

Buffering and PI Server Security

After you enable buffering, it is the buffering application—and not the interface program—that writes data to the PI Server. If the PI Server’s trust table contains a trust entry that allows all applications on an Interface Node to write data, then the buffering application is able write data to the PI Server.

However, if the PI Server contains an interface-specific PI Trust entry that allows a particular interface program to write data, you must have a PI Trust entry specific to buffering. The following are the appropriate entries for the Application Name field of a PI Trust entry:
	Buffering Application
	Application Name field for PI Trust

	PI Buffer Subsystem
	PIBufss.exe

	PI API Buffer Server
	APIBE (if the PI API is using 4 character process names)

APIBUF (if the PI API is using  8 character process names)


To use a process name greater than 4 characters in length for a trust application name, use the LONGAPPNAME=1 in the PIClient.ini file.

Enabling Buffering on an Interface Node with the ICU

The ICU allows you to select either PIBufss or Bufserv as the buffering application for your Interface Node. Run the ICU and select Tools > Buffering.

Choose Buffer Type

[image: image33.png]%y Buffering
Todls

Bufering Settings

Bufered Servers

Pl Buifer Subsystem Service:
Parameter Detalls

AP Bulfer Server Service

Bulfering alows continuous callection of deta on an API Node regarciess of the status of the PI server
orthe nitwork Ik to the server,
& Disable buffeing

" Enable buffering with Pl Buifer Subsystern

e I

Startup ype: Disabled
Number of dependent services: 1
Nurmbe of runing dependent services: 0

" Enable buffering with 4P1 Bulfer Server
Sewvice stalus: Stopped
Startup ype: Disabled
Nurber of dependent services: 0
Nurmbe of uning dependent services: 0

[Eunent Configuraion: Good





To select PIBufss as the buffering application, choose Enable buffering with PI Buffer Subsystem.

To select Bufserv as the buffering application, choose Enable buffering with API Buffer Server. 

If a warning message such as the following appears, click Yes.

[image: image34.png]Changing the buffer type willcause any running nterfaces with a dependercy on
"PI BLffer Subsystem or ‘AP BuFfer Server'to be stopped and restarted.

Are you sure you want to changs from o Buffering' to P1 Buffer Subsystem”

T





Buffering Settings

There are a number of settings that affect the operation of PIBufSS and Bufserv. The Buffering Settings section allows you to set these parameters. If you do not enter values for these parameters, PIBufSS and Bufserv use default values.

PIBufss

For PIBufSS, the paragraphs below describe the settings that may require user intervention. Please contact OSIsoft Technical Support for assistance in further optimizing these and all remaining settings.

[image: image35.png]%y Buffering
Todls

Choase Bulfer Type

Bulfering Settings wil use dafault values uriess other values are specifid.

Buifeed Servers TEHP R

I Bulfer Subsystem Service
Parameler Detalk

AP buter Sarv sorvics Piman memory buffersize Bytes)

Masimum buife e size (KEJ:

Secondary memory buffer size (Bytes}:

Send ate riliseconds)

Rty ate (seconds):

Masimum tansfer obiects:
Masinum theareticalsend rate:

Event queue fle size (MBytes]

Event queus path

Pause tine when bulfers are emply (millseconds):

Maium datarate per server connection (events/sec}:





Primary and Secondary Memory Buffer Size (Bytes)

This is a key parameter for buffering performance. The sum of these two memory buffer sizes must be large enough to accommodate the data that an interface collects during a single scan. A typical event with a Float32 point type requires about 25 bytes. If an interface writes data to 5,000 points, it can potentially send 125,000 bytes (25 * 5000) of data in one scan. As a result, the size of each memory buffer should be 62,500 bytes.

The default value of these memory buffers is 32,768 bytes.

Send rate (milliseconds)

Send rate is the time in milliseconds that PIBufss waits between sending up to the Maximum transfer objects (described below) to the PI Server. The default value is 100. The valid range is 0 to 2,000,000.

Maximum transfer objects

Maximum transfer objects is the maximum number of events that PIBufss sends between each Send rate pause. The default value is 500. The valid range is 1 to 2,000,000.

Event Queue File Size (Mbytes)

This is the size of the event queue files. PIBufss stores the buffered data to these files. The default value is 32. The range is 8 to 131072 (8 to 128 Gbytes). Please see the section entitled, “Queue File Sizing” in the pibufss.chm file for details on how to appropriately size the event queue files.

Event Queue Path

This is the location of the event queue file. The default value is [PIHOME]\DAT.

For optimal performance and reliability, OSIsoft recommends that you place the PIBufss event queue files on a different drive/controller from the system drive and the drive with the Windows paging file. (By default, these two drives are the same.)

Bufserv

For Bufserv, the paragraphs below describe the settings that may require user intervention. Please contact OSIsoft Technical Support for assistance in further optimizing these and all remaining settings.

[image: image36.png]%y Buffering
Todls

Choase Bulfer Type

Bufered Servers

Pl Buifer Subsystem Service:
Parameter Detalls

AP Bulfer Server Service

Bulfering Settings wil use dafault values uriess other values are specifid.

TCPAP Port:

Masimum buife e size (KEJ:

Fiimaty memory bulfer size Bytes}
Secondary memory buffer size (Bytes}:
Send ate riliseconds)

Pause rae (seconds] (4PI Buffr Server)
Rty ate (seconds):

Masimum tansfer obiects:

Masinum theareticalsend rate:





Maximum buffer file size (KB)

This is the maximum size of the buffer file ([PIHOME]\DAT\APIBUF.DAT). When Bufserv cannot communicate with the PI Server, it writes and appends data to this file. When the buffer file reaches this maximum size, Bufserv discards data.

The default value is 2,000,000 KB, which is about 2 GB. The range is from 1 to 2,000,000.

Primary and Secondary Memory Buffer Size (Bytes)

This is a key parameter for buffering performance. The sum of these two memory buffer sizes must be large enough to accommodate the data that an interface collects during a single scan. A typical event with a Float32 point type requires about 25 bytes. If an interface writes data to 5,000 points, it can potentially send 125,000 bytes (25 * 5000) of data in one scan. As a result, the size of each memory buffer should be 62,500 bytes.

The default value of these memory buffers is 32,768 bytes.

Send rate (milliseconds)

Send rate is the time in milliseconds that Bufserv waits between sending up to the Maximum transfer objects (described below) to the PI Server. The default value is 100. The valid range is 0 to 2,000,000.

Maximum transfer objects

Max transfer objects is the maximum number of events that Bufserv sends between each Send rate pause. The default value is 500. The valid range is 1 to 2,000,000.

Buffered Servers

The Buffered Servers section allows you to define the PI Servers or PI Collective that the buffering application writes data.

PIBufss

PIBufss buffers data only to a single PI Server or a PI Collective. Select the PI Server or the PI Collective from the Buffering to collective/server drop down list box.

The following screen shows that PIBufss is configured to write data to a standalone PI Server named starlight. Notice that the Replicate data to all collective member nodes check box is disabled because this PI Server is not part of a collective. (PIBufss automatically detects whether a PI Server is part of a collective.)

[image: image37.png]%y Buffering
Todls

Choase Bulfer Type

Bulfering Settings

Bulfered Servers

Pl Buifer Subsystem Service:
Ferameter Detais @ Pah  C Name

AP Bulfer Server Service

-

Bulfered Server Names

Bulering to collctive/server: [saright =~

1P Addhess
Server
staright

Colective

Member Type.
Nonepicated





The following screen shows that PIBufss is configured to write data to a PI Collective named admiral. By default, PIBufss replicates data to all collective members. That is, it provides n-way buffering.

You can override this option by not checking the Replicate data to all collective member nodes check box. Then, uncheck (or check) the PI Server collective members as desired.

[image: image38.png]%y Buffering
Todls

Choase Bulfer Type

Bulfering Settings

Bulfered Servers

Pl Buifer Subsystem Service:
Parameter Detalls

AP Bulfer Server Service

Bulfering to collctive/server: [adrmial =~
¥ Repicate data o a colctive member nodes
Bulfered Server Names

@ Pah  C Name

1P Addhess
Server

Colctive | Member Type
admialosioftint_admial

Primary

Kemalosisotint admial  Secondary





Bufserv

Bufserv buffers data to a standalone PI Server, or to multiple standalone PI Servers. (If you want to buffer to multiple PI Servers that are part of a PI Collective, you should use PIBufss.)

If the PI Server to which you want Bufserv to buffer data is not in the Server list, enter its name in the Add a server box and click the Add Server button. This PI Server name must be identical to the API Hostname entry:

[image: image39.png]General

Unint
PISDK
Discornested Statup
Debug
Falover
Perfomance Poirts
Perfamance Counters
Healh Pairts

modbusE

Service

10 Rate

Itetface Status

General

PomSouceli [E

yiJ

Sean Classes

Scan Frequency Scan Class #
Gl 1

Pl Host Information

Server/Collctive: etamp330 <
User piadmin
SDK Member:

API Hostname:
Type: Nonepicated - PI3

Version: CErEEs
Descipton

Pt 5450




The following screen shows that Bufserv is configured to write to a standalone PI Server named etamp390. You use this configuration when all the interfaces on the Interface Node write data to etamp390. 

[image: image40.png]%y Buffering
Todls

Choase Bulfer Type Bulfer and Replicate using the follwing conliguraton
Bulfering Settings

Buifered Servers Cick once inthe Bulfered or Repicated colurn o toggle between O and Off.
Pl Bulfer Subsystem Service  Add a server:
Parameter Detalls

AP Bulfer Server Service Server_| Bulfered

Fieplicated
clamp30 Yes  No

staight No  No





The following screen shows that Bufserv is configured to write to two standalone PI Servers, one named etamp390 and the other one named starlight. You use this configuration when some of the interfaces on the Interface Node write data to etamp390 and some write to starlight.

[image: image41.png]%y Buffering
Todls

Choase Bulfer Type Bulfer and Replicate using the follwing conliguraton
Bulfering Settings

Buifered Servers Cick once inthe Bulfered or Repicated colurn o toggle between O and Off.
Pl Bulfer Subsystem Service  Add a server:
Parameter Detalls

Staright
AP Bulfer Server Service Server_| Bulfered

Fieplicated
clamp3 Yes  No

staight Yes  No





Installing Buffering as a Service

Both the PIBufss and Bufserv applications run as a Service.

PI Buffer Subsystem Service

Use the PI Buffer Subsystem Service page to configure PIBufss as a Service. This page also allows you to start and stop the PIBufss service.

PIBufss does not require the logon rights of the local administrator account. It is sufficient to use the LocalSystem account instead. Although the screen below shows asterisks for the LocalSystem password, this account does not have a password.

[image: image42.png]%y Buffering
Todls

Choase Bulfer Type

Bulfering Settings

Bufered Servers

Pl Buifer Subsystem Senvice:
Parameter Detalls

AP Bulfer Server Service

Pl Buifer Subsystem version: 3.4 375,38

Senice name:
Dislay rame:
Logan s
Password
Corfim password

Dependencies:

Dependent services:

Pibufss
Pl Bulfer Subsystem

Locasystern

g

/50
I =
Stopped
St Tpe

© o

© o
 Diats

Create / Remave.





[image: image43.png]&y Buffering

Tk
(Choose et Type e I e ol e [ e
Bulfeing Setings APIBUFFER MAXTRANSFERDBJS int events 50 2000000 5000 Masimum
Buffered Servers APIBUFFER BUF2SIZE int bytes 64 2000000 32768  Secondar
Pl Buffer Subsystem Service | APIBUFFER BUF1SIZE it bytes B4 2000000 32768 Primary AF
SFIBUFFER. MALESIZE - T 20000 2000000 b
i uflr Seve Sevice | APIBLIFEER RETRYRATE Wooxe 0 MO 2 Faweim
AFBUFFER PAUSERATENS 1 mec 0 200000 10 Faseim
SFIBUFFER SENDRATE Wome 0 W00 100 Pawein
AFIBUFFER, GUFFERING oo o 1 0 Tumom:
TR FORT w 1Bmm S0 DefaTl
PBUFSS  MULTISERVER oo o ¢ 0 St
FBURSS  WAFOSTRATE i orerisscc 500 2000000 0 Magmam
FBURSS  QUEUESTZE oo o o @ Newnald
FBURSS  QUELEPATH Sing Diectoy
FBURSS  AUTOCONAIG o O] T e
FBURSS  BUFFERING toa o1 R
< ] >
o =





API Buffer Server Service

Use the API Buffer Server Service page to configure Bufserv as a Service. This page also allows you to start and stop the Bufserv Service

Bufserv version 1.6 and later does not require the logon rights of the local administrator account. It is sufficient to use the LocalSystem account instead. Although the screen below shows asterisks for the LocalSystem password, this account does not have a password.

[image: image44.png]%y Buffering
Todls

Choase Bulfer Type

Bulfering Settings

Bufered Servers

Pl Buifer Subsystem Service:
Parameter Detalls

AP Bulfer Server Service

AP Bulfer Server version: 1.6.1.10

Senice name:
Dislay rame:
Logan s
Password
Corfim password

Dependencies:

Dependent services:

Bufsery
PiBulfer Server

Locasystern

epip

Start/ Stop

P |

Rurring

Stattup Type.
& Ao

© Manual

 Disabled

Create / Remave.






Appendix A:
Error and Informational Messages

A string NameID is pre-pended to error messages written to the message log. Name is a non-configurable identifier that is no longer than 9 characters. ID is a configurable identifier that is no longer than 9 characters and is specified using the /id parameter on the startup command-line. 

Message Logs

The location of the message log depends upon the platform on which the interface is running.  See the UniInt Interface User Manual for more information.

Messages are written to PIHOME\dat\pipc.log at the following times.

· When the interface starts many informational messages are written to the log. These include the version of the interface, the version of UniInt, the command‑line parameters used, and the number of points.

· As the interface retrieves points, messages are sent to the log if there are any problems with the configuration of the points.

· If the /db is used on the command-line, then various informational messages are written to the log file.

Messages

Interface Configuration Error Messages

ERROR> Hardware initialization - C37118XMLConfig::C37118XMLConfig -  Couldn't create XML DOM Schema instance, make sure MSXML 4.0 is installed.
Or
ERROR> Hardware initialization - C37118XMLConfig::C37118XMLConfig -  Couldn't create XML DOM Document instance, make sure MSXML 4.0 is installed.

Or
ERROR> Hardware initialization - C37118XMLConfig::C37118XMLConfig -  Couldn't create XML DOM Schema Collection object, make sure MSXML 4.0 is installed.

There was a problem created one of the DOM XML objects. Typically indicates that the  Microsoft MSXML 4.0 API is not installed. Download the API from Microsoft and install.

ERROR> Hardware initialization - C37118XMLConfig::C37118XMLConfig - XML config document load failed: System error: -2146697210.
The specified XML file could not be loaded. Check the file name and path specified via the /confile argument.

ERROR> Hardware initialization - C37118XMLConfig::C37118XMLConfig -  Couldn't find root <PI_C37_118.Session> element in the XML configuration document. 
The root node root <PI_C37_118.Session> couldn’t be located. Check the format of the XML file. If using the PIC37118 ICU (recommended) this should be correct.
ERROR> Hardware initialization - C37118XMLConfig::C37118XMLConfig - Value for DataSortingAction must be 0, 1, 2 or 3.
Or 

ERROR> Hardware initialization - C37118XMLConfig::C37118XMLConfig - Value for SyncErrorAction must be 0, 1, 2 or 3.

Or

ERROR> Hardware initialization - C37118XMLConfig::C37118XMLConfig - Value for PMUErrorActionmust be 0, 1, 2 or 3.

Or

ERROR> Hardware initialization - C37118XMLConfig::C37118XMLConfig - Value for DataSortingAction must be 0, 1, 2 or 3.
Or
ERROR> Hardware initialization - C37118XMLConfig::C37118XMLConfig - Value for LeapSecondAction must be 0, 1, 2 or 3.

Or
ERROR> Hardware initialization - C37118XMLConfig::C37118XMLConfig - Value for WriteIOTimeout must be 0 or 1.

The value specified for the one of the above attributes in the root section of the XML configuration file is out of range. Use PIC37118 ICU to ensure this value is correct.
ERROR> Hardware initialization - C37118XMLConfig::C37118XMLConfig - No <LocalEndPoint> elements found in the PIC37118_Arbiter_Example.xml XML configuration document.
No <LocalEndPoints> section was found in the configuration document. The must be at least one LocalEndPoints section in the file.

LocalEndPoint::LocalEndPoint( -1 ) - Id attribute missing from LocalEndPoint definition.

The required Id attribute has is missing from a LocalEndPoint section. 
LocalEndPoint::LocalEndPoint( 2 ) - Type element in LocalEndpoint configuration must be IP or Serial.

The Type attribute in LocalEndPoint with Id of 2 has invalid communications type specified. Use the PIC37118 ICU to ensure this attribute is correct.
LocalEndPoint::LocalEndPoint( 2 ) - Invalid data protocol  specified in <DataProtocol>, must be TCP or UDP(case insensitive).
Or
LocalEndPoint::LocalEndPoint( 2 ) - Invalid data protocol  specified in <ConfigProtocol>, must be TCP or UDP(case insensitive).

The DataProtocol or ConfigProtocol attribute must be TCP or UDP. Use the PIC37118 ICU to ensure this attribute is correct. This parameter is not case sensitive. 
Point Loading Error Messages

The following messages are logged when there is a problem loading a point. In each case the point name and point id is reported along with the error information.
LocalEndPoint Id: 1 not found in interface LocalEndPointCollection 
There is not a LocalEndPoint defined in the XML configuration file that matches the Location2 attribute of the tag.
RemoteEndPoint Id: 1 not found in interface RemoteEndPointCollection
There is not a RemoteEndPoint defined in the XML configuration file that matches the Location3 attribute of the tag.

Delimiter character '\' not found in InstrumentTag specification (PMU.FREQ)

The InstrumentTag attribute requires the Measurement Type and Measurement be delimited by a “/” character and was not found.

RemoteEndPoint tag of type LEAPSEC is already defined 
There can only be a single tag of a given RemoteEndPoint type( REP ) for each RemoteEndPoint. For example there can’t be two tags with an InstrumentTag field of REP/LEAPSEC configured for the same RemoteEndPoint. Any subsequent tags are rejected.
PMU Id: 66 not found in interface PMU Collection
The PMU Id specified in the Location5 attribute was not found in the XML configuration file.
Phasor measurement string XX is shorter then shortest valid keyword

Or

Invalid Phasor sub type ( XXX ) specified

The phasor measurement specified in the InstrumentTag attribute is invalid. This value must be PhasorReal, PhasorImag, PhasorMag or PhasorAngle.
Phasor channel ( XXX ) is not configured
Or

Analog channel ( XXX ) is not configured
Or

Digital channel ( XXX ) is not configured
The phasor, analog or digital channel name is not valid for the PMU. This value is not case sensitive but imbedded spaces must remain if they are present in the channel names reported by the PMU. Trailing spaces may be removed.
Phasor tag with channel name of XXX and sub-type of IMAG is already defined for PMU
Or

Analog tag with channel name of XXX is already defined for PMU
Or

Digital tag with channel name of XXX is already defined for PMU
There can only be one PI tag configured for each Analog or Digital channel. Each phasor channel can have one PI tag for each sub type on a channel.
Invalid PMU measurement type ( XXX ) specified
The PMU measurement specified in the InstrumentTag is not valid. For example: PMU/XXX is not valid but PMU/FREQ is.

Communications Related Error Messages

The following messages are logged when there is a problem communications to the C37.118 device. In each case the communications parameters are reported along with the error information.
PDC/PMU communication timeout.

The communications with a PDC or PMU have timed out. The interface will continue to attempt a reconnection.
Error code: -1, Generic Error
The interface was unable to determine the exact nature of the error. Any available information is displayed. 

Debug code: -2, Debug Message.
Miscellaneous debug message.
Error code: -3, Truncated String. 

The C37.118 message was truncated.
Error code: -4, Failed to create communication instance.
The interface was unable to create a communications thread. Check system resources. 

Error code: -5, Bad memory allocation.
A memory allocation occurred in the communications plug-in. Check system resources. 

Error code: -6, Required parameter passed a NULL pointer.
An internal function passed a NULL pointer for a required variable. This should never occur. Contact OSIsoft technical support. 

Error code: -7, Failed to stop communication thread.
The communications thread could not be stopped. This would only occur during interface shutdown, but should never occur. Contact OSIsoft technical support.
Error code: -8, PDC/PMU communication timeout.

The communications with a PDC or PMU have timed out. The interface will continue to attempt a reconnection.

Error code: -9, Sync byte not found.
The 0xAA sync byte was not found in the data stream. The interface will attempt to resynchronize the data stream by closing the socket and reconnecting.
Error code: -10, Message IDCODE not for PDC / PMU. 

The message received was valid but the IDCODE in word 3 of the frame was not for the configured PDC / PMU. Check the XML configuration file and PDC / PMU configuration.
Error code: -11, Message frame size error.
 The frame size in the C37.118 message did not match the actual size.
Error code: -12, Message CRC error. 
The CRC validation failed on a C37.118 message. This error may occur occasionally. If it occurs with any frequency, check the communications hardware.

Error code: -13, No Message Buffer Available.
No message buffer was available. The interface will continue to operate but will be missing data. Contact OSIsoft technical support.  

System Errors and PI Errors

System errors are associated with positive error numbers. Errors related to PI are associated with negative error numbers. 
Error Descriptions on Windows
On Windows, descriptions of system and PI errors can be obtained with the pidiag utility:

Windows:
\PI\adm\pidiag –e error_number
Appendix B: Communication Plug-In Selection 
This appendix describes the selection criteria for the Communications plug-in for the PDCs and PMUs which have been tested. Current Plug-In selections are PIC37118_Comm001, PIC37118_Comm002 and PIC37118_Comm003.
	PDC/PMU
	Data Protocol 
	Command Protocol
	Command and Data on Same Port 
	Data Transmission Mode


	Close Cmd Comm Setting
	Plug-In

	Arbiter 1133
	Udp
	Udp
	Yes
	Unicast
	Yes
	001

	Arbiter 1133
	Tcp
	Tcp
	Yes
	Unicast
	Yes
	001

	Arbiter 1133
	Tcp
	Udp
	No
	Unicast
	Yes
	002

	Arbiter 1133
	Tcp
	Udp
	No
	Broadcast
	Yes
	002

	Arbiter 1133
	Tcp
	Udp
	No
	Multicast
	Yes
	002

	SEL 3306
	Tcp
	Udp
	No
	Unicast
	No
	002

	SEL 421
	Udp
	Udp
	Yes
	Unicast
	Yes
	001

	SEL 421
	Tcp
	Tcp
	Yes
	Unicast
	Yes
	001

	SEL 421
	Tcp
	Udp
	No
	Unicast
	Yes
	002

	SEL 421
	Tcp
	Udp
	No
	Broadcast
	Yes
	002

	SEL 421
	Tcp
	Udp
	No
	Multicast
	Yes
	002

	SEL 451
	Udp
	Udp
	Yes
	Unicast
	Yes
	001

	SEL 451
	Tcp
	Tcp
	Yes
	Unicast
	Yes
	001

	SEL 451
	Tcp
	Udp
	No
	Unicast
	Yes
	002

	SEL 451
	Tcp
	Udp
	No
	Broadcast
	Yes
	002

	SEL 451
	Tcp
	Udp
	No
	Multicast
	Yes
	002

	TVA Proxy
	Udp
	n/a
	n/a
	Unicast
	No
	003

	Serial (All Devices)
	n/a
	n/a
	n/a
	n/a
	No
	001


Revision History

	Date
	Author
	Comments

	13-Jun-2007
	JHartman
	Initial Release

	18-Jul-2007
	JLoe
	Version 1.0.1.3 Revision H: updated headers, table formatting, IORates information

	26-Jul-2007
	MKelly
	Version 1.0.1.3 Revision I: Updated the ICU Control and XML section.  Fixed headers and footers.  Corrected filenames references for csv files included with distribution.

	28-Jun-2008
	JHartman
	Version 1.0.2.0, Added /TagConfig argument information and updated version.

	10-Oct-2008
	MKelly
	Version 1.0.2.0 Revision A; Updated screenshots, replace buffering section, fixed headers and links, updated TOC.

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	


Service installed or uninstalled














Status of the Interface Service





Status of the ICU

















� IEEE stands for the Institute of Electrical & Electronic Engineers.


� A Phasor Measurement Unit (PMU) is a generic device that produces synchronized phasors from voltage and/or current inputs and synchronizing signal.


� A Phasor Data Concentrator provides Phasor data from multiple PMUs.


� A phasor is the complex equivalent of a simple sine wave quantity such that the complex modulus is the sine wave amplitude and complex angle (in polar form) is the sine wave phase angle.






[image: image45.png]

_1232885532.vsd
text


PDC/PMU


PI Data Archive


C37.118 Data	


C37.118 Data	


Communications Plug-In’s


PI Buffering


PI C37.118
Communications Plugin(dll)


PDC/PMU


PDC/PMU


C37.118 Data	


PDC/PMU


PDC/PMU


PDC/PMU


PDC / PMU Model specific Plug-In’s handle differences in application layer implementation between different vendors.


PI Interface Node


PI Server Node


PI API / SDK


PI C37.118 Interface


PI C37.118
Communications Plugin(dll)


PI C37.118
Communications Plugin(dll)



_1236428550.vsd
The height of the text box and its associated line increases or decreases as you add text. To change the width of the comment, drag  the side handle.


PDC or PMU



PI_C37118
Interface


PI Archive


Raw-Data and Timestamp


Process Raw-Data


Update PI System



